## insctructions
TEMPLATE - Rack and Power Allocation Assessment
Rack Attributes from Rack Breakdown - MASTER
Data as of 5/21/2024
| Limit Simulator | Original | Custom
| PDU Max | 375 | 375
| Provider Cap | 0.8 | 0.8
| Safe load | 0.75 | 0.8
| PDU Limit | 225 | 240
| PDU Count | 3 | 3 | Actually 4 but entered 3 for redundancy.
| Zone Limit | 675 | 720
| Even PDU Split | 168.75 | 180
| PDU Pair 1 | 337.5 | 480
| PDU Pair 2 | 337.5 | 240
Refreshing Report Data
To update the data in this report, please use the "Refresh All" button in the Data ribbon. Example below.
Alternatively, the following shortvut keys can be pressed as well.
(Ctrl+Alt+F5)
Filename Format
The filename for the main report should be saved in the following format.
Format: [Site] - Rack and Power Allocation Assessment
Example: DAL10 - Rack and Power Allocation Assessment
For archived files, the following format should be used.
Format: [Site] - Rack and Power Allocation Assessment - [YYYYMMDD]
Example: DAL10 - Rack and Power Allocation Assessment - 20240528
Notes for Creating a New Report
The DC should be changed on the hidden file_path sheet in cell B2.
Once the DC has been updated, the report should be refreshed to get data for the corresponding DC.
When adding zones, it is suggested to space them out 2 rows apart.
When the Row Start box is gray, that means it is formulated. When the box is white, it means the value has been hardcoded.
Template-1 should be used for zones with 4-6 rows and start from left to right then top to bottom.
Template-2 should be used for zones with 4-6 rows and start from top to bottom then left to right.
Template-3 should be used for zones with only 2 or 3 rows.
Limit Simulator
The Limit Simulator below is designed to provide power load scenarios and potential maximum limits on the PDU's and zones. The values below is an example for DAL13.SR03.

## template-1
DAL13.SR01 - Rack and Power Allocation Assessment
Data as of 5/21/2024
| Datacenter | DAL13 |  | Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta | Fast Travel |  | Total | kW | Delta
| Server Room | 1 |  | Zone 1 | 0 | 333.506 | -333.506 | 430 | -430 | 430 | -430 | Go to Zone 1 |  | Live | 443.493 | 4056.507
| Data Hall | Data Hall 4 |  | Zone 2 | 0 | 109.987 | -109.987 | 394 | -394 | 394 | -394 | Go to Zone 2 |  | PK | 824 | 3676
| Leased kW | 4500 | [9 empty] | Go to |  | Rec PK | 824 | 3676
| Power Infra | 400/30/3Phase | [9 empty] | Go to
Go to
Go to
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 1 |  | 333.506 | -333.506 | 430 | -430 | 430 | -430
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 1 | Rack Count | 11 | [5 empty] | Row Start | 12 | Rack Count | 11 |  |  |  |  | Row Start | 23 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 1 | Compute | Hybrid | Live | 32 | 8.281 | 10 |  |  | 12 | Bare Metal | Bare Metal | Live | 20 | 3.96 | 6 |  | 23 | Bare Metal | Bare Metal | Live | 19 | 5.24 | 6
| 2 | Compute | Hybrid | Live | 34 | 9.194 | 10 |  |  | 13 | Bare Metal | Bare Metal | Live | 29 | 5.671 | 6 |  | 24 | Bare Metal | Bare Metal | Live | 23 | 6.351 | 6
| 3 | Compute | Hybrid | Live | 27 | 7.548 | 10 |  |  | 14 | Bare Metal | Bare Metal | Live | 22 | 4.221 | 6 |  | 25 | Bare Metal | Bare Metal | Live | 24 | 6.707 | 6
| 4 | Compute | Hybrid | Live | 32 | 8.958 | 10 |  |  | 15 | Bare Metal | Bare Metal | Live | 21 | 5.326 | 6 |  | 26 | Bare Metal | Bare Metal | Live | 25 | 6.046 | 6
| 5 | Compute | Hybrid | Live | 28 | 8.914 | 10 |  |  | 16 | Bare Metal | Bare Metal | Live | 25 | 5.369 | 6 |  | 27 | Bare Metal | Bare Metal | Live | 26 | 6.35 | 6
| 6 | Network | Aggregate | Live | 0 | 8.436 | 5 |  |  | 17 | Network | Aggregate | Live | 0 | 0 | 5 |  | 28 | Network | Aggregate | Live | 0 | 0 | 5
| 7 | Compute | Hybrid | Live | 27 | 8.005 | 10 |  |  | 18 | Bare Metal | Bare Metal | Live | 28 | 6.073 | 6 |  | 29 | Bare Metal | Bare Metal | Live | 19 | 5.949 | 6
| 8 | Compute | Hybrid | Live | 34 | 8.993 | 10 |  |  | 19 | Bare Metal | Bare Metal | Live | 14 | 3.188 | 6 |  | 30 | Bare Metal | Bare Metal | Live | 29 | 7.789 | 6
| 9 | Compute | Hybrid | Live | 34 | 9.215 | 10 |  |  | 20 | Bare Metal | Bare Metal | Live | 16 | 4.321 | 6 |  | 31 | Bare Metal | Bare Metal | Live | 26 | 7.741 | 6
| 10 | Compute | Hybrid | Live | 37 | 10.059 | 10 |  |  | 21 | Bare Metal | Bare Metal | Live | 15 | 3.875 | 6 |  | 32 | Bare Metal | Bare Metal | Live | 24 | 7.184 | 6
| 11 | Compute | Hybrid | Live | 34 | 9.162 | 10 |  |  | 22 | Bare Metal | COD | Live | 1 | 1.437 | 6 |  | 33 | Bare Metal | Bare Metal | Live | 18 | 6.433 | 6
| Total |  |  |  | 319 | 96.765 | 105 | 105 |  | Total |  |  |  | 191 | 43.441 | 65 | 65 | Total |  |  |  | 233 | 65.79 | 65 | 65
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 34 | Rack Count | 11 | [5 empty] | Row Start | 45 | Rack Count | 11 |  |  |  |  | Row Start | 56 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 34 | Bare Metal | Bare Metal | Live | 21 | 5.21 | 6 |  |  | 45 | Bare Metal | Bare Metal | Live | 15 | 3.315 | 6 |  | 56 | Bare Metal | Bare Metal | Live | 15 | 4.638 | 6
| 35 | Bare Metal | Bare Metal | Live | 20 | 4.349 | 6 |  |  | 46 | Bare Metal | Bare Metal | Live | 15 | 4.318 | 6 |  | 57 | Bare Metal | Bare Metal | Live | 14 | 4.324 | 6
| 36 | Bare Metal | Bare Metal | Live | 23 | 5.399 | 6 |  |  | 47 | Bare Metal | Bare Metal | Live | 13 | 4.21 | 6 |  | 58 | Bare Metal | Bare Metal | Live | 12 | 4.353 | 6
| 37 | Bare Metal | Bare Metal | Live | 22 | 3.894 | 6 |  |  | 48 | Bare Metal | Bare Metal | Live | 12 | 2.805 | 6 |  | 59 | Bare Metal | Bare Metal | Live | 22 | 6.184 | 6
| 38 | Bare Metal | Bare Metal | Live | 18 | 4.331 | 6 |  |  | 49 | Bare Metal | Bare Metal | Live | 11 | 3.775 | 6 |  | 60 | Bare Metal | Bare Metal | Live | 21 | 4.964 | 6
| 39 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 50 | Network | Aggregate | Live | 0 | 0 | 5 |  | 61 | Network | Aggregate | Live | 0 | 0 | 5
| 40 | Bare Metal | Bare Metal | Live | 24 | 4.299 | 6 |  |  | 51 | Bare Metal | Bare Metal | Live | 12 | 2.85 | 6 |  | 62 | Bare Metal | Bare Metal | Live | 18 | 4.363 | 6
| 41 | Bare Metal | Bare Metal | Live | 24 | 5.957 | 6 |  |  | 52 | Bare Metal | Bare Metal | Live | 13 | 2.928 | 6 |  | 63 | Bare Metal | Bare Metal | Live | 10 | 3.675 | 6
| 42 | Bare Metal | Bare Metal | Live | 18 | 3.214 | 6 |  |  | 53 | Bare Metal | Bare Metal | Live | 13 | 3.102 | 6 |  | 64 | Bare Metal | Bare Metal | Live | 16 | 4.632 | 6
| 43 | Bare Metal | Bare Metal | Live | 23 | 4.008 | 6 |  |  | 54 | Bare Metal | Bare Metal | Live | 14 | 3.627 | 6 |  | 65 | Bare Metal | Bare Metal | Live | 15 | 3.078 | 6
| 44 | Bare Metal | Bare Metal | Live | 25 | 4.983 | 6 |  |  | 55 | Bare Metal | Bare Metal | Live | 15 | 3.286 | 6 |  | 66 | Bare Metal | Bare Metal | Live | 29 | 7.439 | 6
| Total |  |  |  | 218 | 45.644 | 65 | 65 |  | Total |  |  |  | 133 | 34.216 | 65 | 65 | Total |  |  |  | 172 | 47.65 | 65 | 65
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 2 |  | 109.987 | -109.987 | 394 | -394 | 394 | -394
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 67 | Rack Count | 11 | [5 empty] | Row Start | 78 | Rack Count | 11 |  |  |  |  | Row Start | 89 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 67 | Bare Metal | Bare Metal | Live | 13 | 3.397 | 6 |  |  | 78 | Bare Metal | Bare Metal | Live | 18 | 4.45 | 6 |  | 89 | Storage | File/Block | Live | 0 | 0 | 6
| 68 | Bare Metal | Bare Metal | Live | 25 | 6.119 | 6 |  |  | 79 | Bare Metal | Bare Metal | Live | 18 | 4.856 | 6 |  | 90 | Storage | File/Block | Live | 0 | 0 | 6
| 69 | Bare Metal | Bare Metal | Live | 30 | 7.987 | 6 |  |  | 80 | Bare Metal | Bare Metal | Live | 16 | 3.779 | 6 |  | 91 | Storage | File/Block | Live | 3 | 0 | 6
| 70 | Bare Metal | Bare Metal | Live | 22 | 7.014 | 6 |  |  | 81 | Bare Metal | Bare Metal | Live | 20 | 3.872 | 6 |  | 92 | Storage | File/Block | Live | 7 | 0 | 6
| 71 | Bare Metal | Bare Metal | Live | 17 | 3.642 | 6 |  |  | 82 | Bare Metal | Bare Metal | Live | 19 | 3.468 | 6 |  | 93 | Storage | File/Block | Live | 0 | 0 | 6
| 72 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 83 | Network | Aggregate | Live | 0 | 0 | 5 |  | 94 | Storage | File/Block | Live | 1 | 0 | 6
| 73 | Bare Metal | Bare Metal | Live | 18 | 3.756 | 6 |  |  | 84 | Bare Metal | Bare Metal | Live | 21 | 5.209 | 6 |  | 95 | Storage | File/Block | Live | 16 | 0 | 6
| 74 | Bare Metal | Bare Metal | Live | 23 | 4.568 | 6 |  |  | 85 | Bare Metal | Bare Metal | Live | 22 | 6.207 | 6 |  | 96 | Storage | File/Block | Live | 19 | 0 | 6
| 75 | Bare Metal | Bare Metal | Live | 21 | 4.748 | 6 |  |  | 86 | Bare Metal | Bare Metal | Live | 32 | 8.965 | 6 |  | 97 | Storage | File/Block | Live | 0 | 0 | 6
| 76 | Bare Metal | Bare Metal | Live | 31 | 6.303 | 6 |  |  | 87 | Bare Metal | Bare Metal | Live | 17 | 5.467 | 6 |  | 98 | Storage | File/Block | Live | 3 | 0 | 6
| 77 | Bare Metal | Bare Metal | Live | 31 | 8.328 | 6 |  |  | 88 | Bare Metal | Bare Metal | Live | 34 | 7.852 | 6 |  | 99 | Storage | File/Block | Live | 7 | 0 | 6
| Total |  |  |  | 231 | 55.862 | 65 | 65 |  | Total |  |  |  | 217 | 54.125 | 65 | 65 | Total |  |  |  | 56 | 0 | 66 | 66
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 100 | Rack Count | 11 | [5 empty] | Row Start | 111 | Rack Count | 11 |  |  |  |  | Row Start | 122 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 100 | Storage | COS | Live | 15 | 0 | 6 |  |  | 111 | Storage | File/Block | Live | 3 | 0 | 6 |  | 122 | Storage | COS | Live | 13 | 0 | 6
| 101 | Storage | COS | Live | 13 | 0 | 6 |  |  | 112 | Storage | File/Block | Live | 3 | 0 | 6 |  | 123 | Storage | COS | Live | 11 | 0 | 6
| 102 | Storage | COS | Live | 12 | 0 | 6 |  |  | 113 | Storage | File/Block | Live | 15 | 0 | 6 |  | 124 | Storage | COS | Live | 10 | 0 | 6
| 103 | Storage | COS | Live | 14 | 0 | 6 |  |  | 114 | Storage | File/Block | Live | 15 | 0 | 6 |  | 125 | Storage | COS | Live | 10 | 0 | 6
| 104 | Storage | COS | Live | 15 | 0 | 6 |  |  | 115 | Storage | File/Block | Live | 4 | 0 | 6 |  | 126 | Storage | COS | Live | 12 | 0 | 6
| 105 | Storage | COS | Live | 16 | 0 | 6 |  |  | 116 | Storage | File/Block | Live | 2 | 0 | 6 |  | 127 | Storage | COS | Live | 14 | 0 | 6
| 106 | Storage | COS | Live | 14 | 0 | 6 |  |  | 117 | Storage | File/Block | Live | 14 | 0 | 6 |  | 128 | Storage | COS | Live | 13 | 0 | 6
| 107 | Storage | COS | Live | 14 | 0 | 6 |  |  | 118 | Storage | File/Block | Live | 11 | 0 | 6 |  | 129 | Storage | COS | Live | 9 | 0 | 6
| 108 | Storage | COS | Live | 12 | 0 | 6 |  |  | 119 | Storage | File/Block | Live | 11 | 0 | 6 |  | 130 | Storage | COS | Live | 10 | 0 | 6
| 109 | Storage | COS | Live | 13 | 0 | 6 |  |  | 120 | Storage | File/Block | Live | 10 | 0 | 6 |  | 131 | Storage | COS | Live | 11 | 0 | 6
| 110 | Storage | COS | Live | 15 | 0 | 6 |  |  | 121 | Storage | File/Block | Live | 10 | 0 | 6 |  | 132 | Storage | COS | Live | 13 | 0 | 6
| Total |  |  |  | 153 | 0 | 66 | 66 |  | Total |  |  |  | 98 | 0 | 66 | 66 | Total |  |  |  | 126 | 0 | 66 | 66

## template-2
DAL13.SR01 - Rack and Power Allocation Assessment
Data as of 5/21/2024
| Datacenter | DAL13 |  | Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta | Fast Travel |  | Total | kW | Delta
| Server Room | 1 |  | Zone 1 | 0 | 333.506 | -333.506 | 430 | -430 | 430 | -430 | Go to Zone 1 |  | Live | 443.493 | 4056.507
| Data Hall | Data Hall 4 |  | Zone 2 | 500 | 109.987 | 390.013 | 394 | 106 | 394 | 106 | Go to Zone 2 |  | PK | 824 | 3676
| Leased kW | 4500 | [9 empty] | Go to |  | Rec PK | 824 | 3676
| Power Infra | 400/30/3Phase | [9 empty] | Go to
Go to
Go to
Go to
Go to
Go to
|  |  |  | Zone 10 | #REF! | [6 empty] | #N/A
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 1 |  | 333.506 | -333.506 | 430 | -430 | 430 | -430
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 1 | Rack Count | 11 | [5 empty] | Row Start | 23 | Rack Count | 11 |  |  |  |  | Row Start | 45 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 1 | Compute | Hybrid | Live | 32 | 8.281 | 10 |  |  | 23 | Bare Metal | Bare Metal | Live | 19 | 5.24 | 6 |  | 45 | Bare Metal | Bare Metal | Live | 15 | 3.315 | 6
| 2 | Compute | Hybrid | Live | 34 | 9.194 | 10 |  |  | 24 | Bare Metal | Bare Metal | Live | 23 | 6.351 | 6 |  | 46 | Bare Metal | Bare Metal | Live | 15 | 4.318 | 6
| 3 | Compute | Hybrid | Live | 27 | 7.548 | 10 |  |  | 25 | Bare Metal | Bare Metal | Live | 24 | 6.707 | 6 |  | 47 | Bare Metal | Bare Metal | Live | 13 | 4.21 | 6
| 4 | Compute | Hybrid | Live | 32 | 8.958 | 10 |  |  | 26 | Bare Metal | Bare Metal | Live | 25 | 6.046 | 6 |  | 48 | Bare Metal | Bare Metal | Live | 12 | 2.805 | 6
| 5 | Compute | Hybrid | Live | 28 | 8.914 | 10 |  |  | 27 | Bare Metal | Bare Metal | Live | 26 | 6.35 | 6 |  | 49 | Bare Metal | Bare Metal | Live | 11 | 3.775 | 6
| 6 | Network | Aggregate | Live | 0 | 8.436 | 5 |  |  | 28 | Network | Aggregate | Live | 0 | 0 | 5 |  | 50 | Network | Aggregate | Live | 0 | 0 | 5
| 7 | Compute | Hybrid | Live | 27 | 8.005 | 10 |  |  | 29 | Bare Metal | Bare Metal | Live | 19 | 5.949 | 6 |  | 51 | Bare Metal | Bare Metal | Live | 12 | 2.85 | 6
| 8 | Compute | Hybrid | Live | 34 | 8.993 | 10 |  |  | 30 | Bare Metal | Bare Metal | Live | 29 | 7.789 | 6 |  | 52 | Bare Metal | Bare Metal | Live | 13 | 2.928 | 6
| 9 | Compute | Hybrid | Live | 34 | 9.215 | 10 |  |  | 31 | Bare Metal | Bare Metal | Live | 26 | 7.741 | 6 |  | 53 | Bare Metal | Bare Metal | Live | 13 | 3.102 | 6
| 10 | Compute | Hybrid | Live | 37 | 10.059 | 10 |  |  | 32 | Bare Metal | Bare Metal | Live | 24 | 7.184 | 6 |  | 54 | Bare Metal | Bare Metal | Live | 14 | 3.627 | 6
| 11 | Compute | Hybrid | Live | 34 | 9.162 | 10 |  |  | 33 | Bare Metal | Bare Metal | Live | 18 | 6.433 | 6 |  | 55 | Bare Metal | Bare Metal | Live | 15 | 3.286 | 6
| Total |  |  |  | 319 | 96.765 | 105 | 105 |  | Total |  |  |  | 233 | 65.79 | 65 | 65 | Total |  |  |  | 133 | 34.216 | 65 | 65
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 12 | Rack Count | 11 | [5 empty] | Row Start | 34 | Rack Count | 11 |  |  |  |  | Row Start | 56 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 12 | Bare Metal | Bare Metal | Live | 20 | 3.96 | 6 |  |  | 34 | Bare Metal | Bare Metal | Live | 21 | 5.21 | 6 |  | 56 | Bare Metal | Bare Metal | Live | 15 | 4.638 | 6
| 13 | Bare Metal | Bare Metal | Live | 29 | 5.671 | 6 |  |  | 35 | Bare Metal | Bare Metal | Live | 20 | 4.349 | 6 |  | 57 | Bare Metal | Bare Metal | Live | 14 | 4.324 | 6
| 14 | Bare Metal | Bare Metal | Live | 22 | 4.221 | 6 |  |  | 36 | Bare Metal | Bare Metal | Live | 23 | 5.399 | 6 |  | 58 | Bare Metal | Bare Metal | Live | 12 | 4.353 | 6
| 15 | Bare Metal | Bare Metal | Live | 21 | 5.326 | 6 |  |  | 37 | Bare Metal | Bare Metal | Live | 22 | 3.894 | 6 |  | 59 | Bare Metal | Bare Metal | Live | 22 | 6.184 | 6
| 16 | Bare Metal | Bare Metal | Live | 25 | 5.369 | 6 |  |  | 38 | Bare Metal | Bare Metal | Live | 18 | 4.331 | 6 |  | 60 | Bare Metal | Bare Metal | Live | 21 | 4.964 | 6
| 17 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 39 | Network | Aggregate | Live | 0 | 0 | 5 |  | 61 | Network | Aggregate | Live | 0 | 0 | 5
| 18 | Bare Metal | Bare Metal | Live | 28 | 6.073 | 6 |  |  | 40 | Bare Metal | Bare Metal | Live | 24 | 4.299 | 6 |  | 62 | Bare Metal | Bare Metal | Live | 18 | 4.363 | 6
| 19 | Bare Metal | Bare Metal | Live | 14 | 3.188 | 6 |  |  | 41 | Bare Metal | Bare Metal | Live | 24 | 5.957 | 6 |  | 63 | Bare Metal | Bare Metal | Live | 10 | 3.675 | 6
| 20 | Bare Metal | Bare Metal | Live | 16 | 4.321 | 6 |  |  | 42 | Bare Metal | Bare Metal | Live | 18 | 3.214 | 6 |  | 64 | Bare Metal | Bare Metal | Live | 16 | 4.632 | 6
| 21 | Bare Metal | Bare Metal | Live | 15 | 3.875 | 6 |  |  | 43 | Bare Metal | Bare Metal | Live | 23 | 4.008 | 6 |  | 65 | Bare Metal | Bare Metal | Live | 15 | 3.078 | 6
| 22 | Bare Metal | COD | Live | 1 | 1.437 | 6 |  |  | 44 | Bare Metal | Bare Metal | Live | 25 | 4.983 | 6 |  | 66 | Bare Metal | Bare Metal | Live | 29 | 7.439 | 6
| Total |  |  |  | 191 | 43.441 | 65 | 65 |  | Total |  |  |  | 218 | 45.644 | 65 | 65 | Total |  |  |  | 172 | 47.65 | 65 | 65
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 2 | 500 | 109.987 | 390.013 | 394 | 106 | 394 | 106
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 67 | Rack Count | 11 | [5 empty] | Row Start | 89 | Rack Count | 11 |  |  |  |  | Row Start | 111 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 67 | Bare Metal | Bare Metal | Live | 13 | 3.397 | 6 |  |  | 89 | Storage | File/Block | Live | 0 | 0 | 6 |  | 111 | Storage | File/Block | Live | 3 | 0 | 6
| 68 | Bare Metal | Bare Metal | Live | 25 | 6.119 | 6 |  |  | 90 | Storage | File/Block | Live | 0 | 0 | 6 |  | 112 | Storage | File/Block | Live | 3 | 0 | 6
| 69 | Bare Metal | Bare Metal | Live | 30 | 7.987 | 6 |  |  | 91 | Storage | File/Block | Live | 3 | 0 | 6 |  | 113 | Storage | File/Block | Live | 15 | 0 | 6
| 70 | Bare Metal | Bare Metal | Live | 22 | 7.014 | 6 |  |  | 92 | Storage | File/Block | Live | 7 | 0 | 6 |  | 114 | Storage | File/Block | Live | 15 | 0 | 6
| 71 | Bare Metal | Bare Metal | Live | 17 | 3.642 | 6 |  |  | 93 | Storage | File/Block | Live | 0 | 0 | 6 |  | 115 | Storage | File/Block | Live | 4 | 0 | 6
| 72 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 94 | Storage | File/Block | Live | 1 | 0 | 6 |  | 116 | Storage | File/Block | Live | 2 | 0 | 6
| 73 | Bare Metal | Bare Metal | Live | 18 | 3.756 | 6 |  |  | 95 | Storage | File/Block | Live | 16 | 0 | 6 |  | 117 | Storage | File/Block | Live | 14 | 0 | 6
| 74 | Bare Metal | Bare Metal | Live | 23 | 4.568 | 6 |  |  | 96 | Storage | File/Block | Live | 19 | 0 | 6 |  | 118 | Storage | File/Block | Live | 11 | 0 | 6
| 75 | Bare Metal | Bare Metal | Live | 21 | 4.748 | 6 |  |  | 97 | Storage | File/Block | Live | 0 | 0 | 6 |  | 119 | Storage | File/Block | Live | 11 | 0 | 6
| 76 | Bare Metal | Bare Metal | Live | 31 | 6.303 | 6 |  |  | 98 | Storage | File/Block | Live | 3 | 0 | 6 |  | 120 | Storage | File/Block | Live | 10 | 0 | 6
| 77 | Bare Metal | Bare Metal | Live | 31 | 8.328 | 6 |  |  | 99 | Storage | File/Block | Live | 7 | 0 | 6 |  | 121 | Storage | File/Block | Live | 10 | 0 | 6
| Total |  |  |  | 231 | 55.862 | 65 | 65 |  | Total |  |  |  | 56 | 0 | 66 | 66 | Total |  |  |  | 98 | 0 | 66 | 66
| Note | [8 empty] | Note | [7 empty] | Note
| Row Start | 78 | Rack Count | 11 | [5 empty] | Row Start | 100 | Rack Count | 11 |  |  |  |  | Row Start | 122 | Rack Count | 11
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 78 | Bare Metal | Bare Metal | Live | 18 | 4.45 | 6 |  |  | 100 | Storage | COS | Live | 15 | 0 | 6 |  | 122 | Storage | COS | Live | 13 | 0 | 6
| 79 | Bare Metal | Bare Metal | Live | 18 | 4.856 | 6 |  |  | 101 | Storage | COS | Live | 13 | 0 | 6 |  | 123 | Storage | COS | Live | 11 | 0 | 6
| 80 | Bare Metal | Bare Metal | Live | 16 | 3.779 | 6 |  |  | 102 | Storage | COS | Live | 12 | 0 | 6 |  | 124 | Storage | COS | Live | 10 | 0 | 6
| 81 | Bare Metal | Bare Metal | Live | 20 | 3.872 | 6 |  |  | 103 | Storage | COS | Live | 14 | 0 | 6 |  | 125 | Storage | COS | Live | 10 | 0 | 6
| 82 | Bare Metal | Bare Metal | Live | 19 | 3.468 | 6 |  |  | 104 | Storage | COS | Live | 15 | 0 | 6 |  | 126 | Storage | COS | Live | 12 | 0 | 6
| 83 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 105 | Storage | COS | Live | 16 | 0 | 6 |  | 127 | Storage | COS | Live | 14 | 0 | 6
| 84 | Bare Metal | Bare Metal | Live | 21 | 5.209 | 6 |  |  | 106 | Storage | COS | Live | 14 | 0 | 6 |  | 128 | Storage | COS | Live | 13 | 0 | 6
| 85 | Bare Metal | Bare Metal | Live | 22 | 6.207 | 6 |  |  | 107 | Storage | COS | Live | 14 | 0 | 6 |  | 129 | Storage | COS | Live | 9 | 0 | 6
| 86 | Bare Metal | Bare Metal | Live | 32 | 8.965 | 6 |  |  | 108 | Storage | COS | Live | 12 | 0 | 6 |  | 130 | Storage | COS | Live | 10 | 0 | 6
| 87 | Bare Metal | Bare Metal | Live | 17 | 5.467 | 6 |  |  | 109 | Storage | COS | Live | 13 | 0 | 6 |  | 131 | Storage | COS | Live | 11 | 0 | 6
| 88 | Bare Metal | Bare Metal | Live | 34 | 7.852 | 6 |  |  | 110 | Storage | COS | Live | 15 | 0 | 6 |  | 132 | Storage | COS | Live | 13 | 0 | 6
| Total |  |  |  | 217 | 54.125 | 65 | 65 |  | Total |  |  |  | 153 | 0 | 66 | 66 | Total |  |  |  | 126 | 0 | 66 | 66

## template-3
DAL13.SR01 - Rack and Power Allocation Assessment
Data as of 5/21/2024
| Datacenter | DAL13 |  | Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta | Fast Travel |  | Total | kW | Delta
| Server Room | 1 |  | Zone 1 | 0 | 151.797 | -151.797 | 182 | -182 | 182 | -182 | Go to Zone 1 |  | Live | 443.493 | 4056.507
| Data Hall | Data Hall 4 |  | Zone 2 | 0 | 114.491 | -114.491 | 142 | -142 | 142 | -142 | Go to Zone 2 |  | PK | 608 | 3892
| Leased kW | 4500 |  | Zone 3 | 0 | 95.377 | -95.377 | 141 | -141 | 141 | -141 | Go to Zone 3 |  | Rec PK | 608 | 3892
| Power Infra | 400/30/3Phase |  | Zone 4 | 0 | 81.828 | -81.828 | 143 | -143 | 143 | -143 | Go to Zone 4
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 1 |  | 151.797 | -151.797 | 182 | -182 | 182 | -182
| Note | [8 empty] | Note
| Row Start | 1 | Rack Count | 12 | [5 empty] | Row Start | 13 | Rack Count | 12
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 1 | Compute | Hybrid | Live | 32 | 8.281 | 10 |  |  | 13 | Bare Metal | Bare Metal | Live | 29 | 5.671 | 6
| 2 | Compute | Hybrid | Live | 34 | 9.194 | 10 |  |  | 14 | Bare Metal | Bare Metal | Live | 22 | 4.221 | 6
| 3 | Compute | Hybrid | Live | 27 | 7.548 | 10 |  |  | 15 | Bare Metal | Bare Metal | Live | 21 | 5.326 | 6
| 4 | Compute | Hybrid | Live | 32 | 8.958 | 10 |  |  | 16 | Bare Metal | Bare Metal | Live | 25 | 5.369 | 6
| 5 | Compute | Hybrid | Live | 28 | 8.914 | 10 |  |  | 17 | Network | Aggregate | Live | 0 | 0 | 5
| 6 | Network | Aggregate | Live | 0 | 8.436 | 5 |  |  | 18 | Bare Metal | Bare Metal | Live | 28 | 6.073 | 6
| 7 | Compute | Hybrid | Live | 27 | 8.005 | 10 |  |  | 19 | Bare Metal | Bare Metal | Live | 14 | 3.188 | 6
| 8 | Compute | Hybrid | Live | 34 | 8.993 | 10 |  |  | 20 | Bare Metal | Bare Metal | Live | 16 | 4.321 | 6
| 9 | Compute | Hybrid | Live | 34 | 9.215 | 10 |  |  | 21 | Bare Metal | Bare Metal | Live | 15 | 3.875 | 6
| 10 | Compute | Hybrid | Live | 37 | 10.059 | 10 |  |  | 22 | Bare Metal | COD | Live | 1 | 1.437 | 6
| 11 | Compute | Hybrid | Live | 34 | 9.162 | 10 |  |  | 23 | Bare Metal | Bare Metal | Live | 19 | 5.24 | 6
| 12 | Bare Metal | Bare Metal | Live | 20 | 3.96 | 6 |  |  | 24 | Bare Metal | Bare Metal | Live | 23 | 6.351 | 6
| Total |  |  |  | 339 | 100.725 | 111 | 111 |  | Total |  |  |  | 213 | 51.072 | 71 | 71
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 2 |  | 114.491 | -114.491 | 142 | -142 | 142 | -142
| Note | [8 empty] | Note
| Row Start | 25 | Rack Count | 12 | [5 empty] | Row Start | 37 | Rack Count | 12
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 25 | Bare Metal | Bare Metal | Live | 24 | 6.707 | 6 |  |  | 37 | Bare Metal | Bare Metal | Live | 22 | 3.894 | 6
| 26 | Bare Metal | Bare Metal | Live | 25 | 6.046 | 6 |  |  | 38 | Bare Metal | Bare Metal | Live | 18 | 4.331 | 6
| 27 | Bare Metal | Bare Metal | Live | 26 | 6.35 | 6 |  |  | 39 | Network | Aggregate | Live | 0 | 0 | 5
| 28 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 40 | Bare Metal | Bare Metal | Live | 24 | 4.299 | 6
| 29 | Bare Metal | Bare Metal | Live | 19 | 5.949 | 6 |  |  | 41 | Bare Metal | Bare Metal | Live | 24 | 5.957 | 6
| 30 | Bare Metal | Bare Metal | Live | 29 | 7.789 | 6 |  |  | 42 | Bare Metal | Bare Metal | Live | 18 | 3.214 | 6
| 31 | Bare Metal | Bare Metal | Live | 26 | 7.741 | 6 |  |  | 43 | Bare Metal | Bare Metal | Live | 23 | 4.008 | 6
| 32 | Bare Metal | Bare Metal | Live | 24 | 7.184 | 6 |  |  | 44 | Bare Metal | Bare Metal | Live | 25 | 4.983 | 6
| 33 | Bare Metal | Bare Metal | Live | 18 | 6.433 | 6 |  |  | 45 | Bare Metal | Bare Metal | Live | 15 | 3.315 | 6
| 34 | Bare Metal | Bare Metal | Live | 21 | 5.21 | 6 |  |  | 46 | Bare Metal | Bare Metal | Live | 15 | 4.318 | 6
| 35 | Bare Metal | Bare Metal | Live | 20 | 4.349 | 6 |  |  | 47 | Bare Metal | Bare Metal | Live | 13 | 4.21 | 6
| 36 | Bare Metal | Bare Metal | Live | 23 | 5.399 | 6 |  |  | 48 | Bare Metal | Bare Metal | Live | 12 | 2.805 | 6
| Total |  |  |  | 255 | 69.157 | 71 | 71 |  | Total |  |  |  | 209 | 45.334 | 71 | 71
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 3 |  | 95.377 | -95.377 | 141 | -141 | 141 | -141
| Note | [8 empty] | Note
| Row Start | 49 | Rack Count | 12 | [5 empty] | Row Start | 61 | Rack Count | 12
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 49 | Bare Metal | Bare Metal | Live | 11 | 3.775 | 6 |  |  | 61 | Network | Aggregate | Live | 0 | 0 | 5
| 50 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 62 | Bare Metal | Bare Metal | Live | 18 | 4.363 | 6
| 51 | Bare Metal | Bare Metal | Live | 12 | 2.85 | 6 |  |  | 63 | Bare Metal | Bare Metal | Live | 10 | 3.675 | 6
| 52 | Bare Metal | Bare Metal | Live | 13 | 2.928 | 6 |  |  | 64 | Bare Metal | Bare Metal | Live | 16 | 4.632 | 6
| 53 | Bare Metal | Bare Metal | Live | 13 | 3.102 | 6 |  |  | 65 | Bare Metal | Bare Metal | Live | 15 | 3.078 | 6
| 54 | Bare Metal | Bare Metal | Live | 14 | 3.627 | 6 |  |  | 66 | Bare Metal | Bare Metal | Live | 29 | 7.439 | 6
| 55 | Bare Metal | Bare Metal | Live | 15 | 3.286 | 6 |  |  | 67 | Bare Metal | Bare Metal | Live | 13 | 3.397 | 6
| 56 | Bare Metal | Bare Metal | Live | 15 | 4.638 | 6 |  |  | 68 | Bare Metal | Bare Metal | Live | 25 | 6.119 | 6
| 57 | Bare Metal | Bare Metal | Live | 14 | 4.324 | 6 |  |  | 69 | Bare Metal | Bare Metal | Live | 30 | 7.987 | 6
| 58 | Bare Metal | Bare Metal | Live | 12 | 4.353 | 6 |  |  | 70 | Bare Metal | Bare Metal | Live | 22 | 7.014 | 6
| 59 | Bare Metal | Bare Metal | Live | 22 | 6.184 | 6 |  |  | 71 | Bare Metal | Bare Metal | Live | 17 | 3.642 | 6
| 60 | Bare Metal | Bare Metal | Live | 21 | 4.964 | 6 |  |  | 72 | Network | Aggregate | Live | 0 | 0 | 5
| Total |  |  |  | 162 | 44.031 | 71 | 71 |  | Total |  |  |  | 195 | 51.346 | 70 | 70
| Zone | Limit | Live | Delta | PK | Delta | Rec PK | Delta
| Zone 4 |  | 81.828 | -81.828 | 143 | -143 | 143 | -143
| Note | [8 empty] | Note
| Row Start | 73 | Rack Count | 12 | [5 empty] | Row Start | 85 | Rack Count | 12
| Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK |  | Rack | Type | Sub-Type | Status | HW Count | Live | PK | Rec PK
| 73 | Bare Metal | Bare Metal | Live | 18 | 3.756 | 6 |  |  | 85 | Bare Metal | Bare Metal | Live | 22 | 6.207 | 6
| 74 | Bare Metal | Bare Metal | Live | 23 | 4.568 | 6 |  |  | 86 | Bare Metal | Bare Metal | Live | 32 | 8.965 | 6
| 75 | Bare Metal | Bare Metal | Live | 21 | 4.748 | 6 |  |  | 87 | Bare Metal | Bare Metal | Live | 17 | 5.467 | 6
| 76 | Bare Metal | Bare Metal | Live | 31 | 6.303 | 6 |  |  | 88 | Bare Metal | Bare Metal | Live | 34 | 7.852 | 6
| 77 | Bare Metal | Bare Metal | Live | 31 | 8.328 | 6 |  |  | 89 | Storage | File/Block | Live | 0 | 0 | 6
| 78 | Bare Metal | Bare Metal | Live | 18 | 4.45 | 6 |  |  | 90 | Storage | File/Block | Live | 0 | 0 | 6
| 79 | Bare Metal | Bare Metal | Live | 18 | 4.856 | 6 |  |  | 91 | Storage | File/Block | Live | 0 | 0 | 6
| 80 | Bare Metal | Bare Metal | Live | 16 | 3.779 | 6 |  |  | 92 | Storage | File/Block | Live | 0 | 0 | 6
| 81 | Bare Metal | Bare Metal | Live | 20 | 3.872 | 6 |  |  | 93 | Storage | File/Block | Live | 0 | 0 | 6
| 82 | Bare Metal | Bare Metal | Live | 19 | 3.468 | 6 |  |  | 94 | Storage | File/Block | Live | 0 | 0 | 6
| 83 | Network | Aggregate | Live | 0 | 0 | 5 |  |  | 95 | Storage | File/Block | Live | 0 | 0 | 6
| 84 | Bare Metal | Bare Metal | Live | 21 | 5.209 | 6 |  |  | 96 | Storage | File/Block | Live | 0 | 0 | 6
| Total |  |  |  | 236 | 53.337 | 71 | 71 |  | Total |  |  |  | 105 | 28.491 | 72 | 72

## rack_breakdown
Rack Path | Data Center | Server Room | Rack | Pod | Speed | Path | Group | Type | Sub-Type | Status | Max Slots | Rack ID | kW/Rack | Utility Identifier | Lease Identifier | Zone-Power | Row Number | Notes | Column1 | Active Servers | Active Hardware | Current Inventory | Current Spare Pool | Adjusted Inventory | Current Other | Total Servers | Total Hardware | Adj Max Slots | Active Slots | Inventory Slots | Other Slots | Used Slots | Spare Pool Slots | Usable Slots | Unused Slots | Unused + Inventory | Unused + Inv + Other | Unusable Slots | Avg kW per Slot: | Reserved Power | Spare Pool Power | Type - Status | Empty Flag | POD Code | G | H | J | K | Total | kW per Active Slot | Est. Total Rack kW | Power Strip Errors | Est kW Remaining | Est. Slots Remaining | Start/End Rack ID | Empty Rack Count | Row
dal13.sr01.rk01 | DAL13 | 1 | 1 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108409 | 10 | 1 | L1 | Z1-375 | 1 | acoleman - Restricted Access Account - Hardware Unlocked |  | 32 | 37 | 2 | 0 | 2 | 2 | 36 | 41 | 50 | 37 | 2 | 2 | 41 | 0 | 13 | 9 | 11 | 13 | 0 | 0.2 | 1 | 0 | Compute - Live | N | DAL13-101 | 5463 | 2818 | 0 | 0 | 8.281 | 0.22381 | 9.1762 |  | 0.82376 | 3.6806 | S | 0 | -
dal13.sr01.rk02 | DAL13 | 1 | 2 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108411 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 34 | 39 | 1 | 0 | 1 | 0 | 35 | 40 | 50 | 39 | 1 | 0 | 40 | 0 | 11 | 10 | 11 | 11 | 0 | 0.2 | 1 | 0 | Compute - Live | N | DAL13-101 | 5365 | 3829 | 0 | 0 | 9.194 | 0.23574 | 9.4297 |  | 0.57026 | 2.419 | - | 0 | -
dal13.sr01.rk03 | DAL13 | 1 | 3 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108413 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 27 | 32 | 1 | 0 | 1 | 1 | 29 | 34 | 50 | 32 | 1 | 1 | 34 | 0 | 18 | 16 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Compute - Live | N | DAL13-101 | 2527 | 5021 | 0 | 0 | 7.548 | 0.23588 | 8.0198 |  | 1.9802 | 8.3953 | - | 0 | -
dal13.sr01.rk04 | DAL13 | 1 | 4 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108415 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 32 | 37 | 1 | 0 | 1 | 0 | 33 | 38 | 50 | 37 | 1 | 0 | 38 | 0 | 13 | 12 | 13 | 13 | 0 | 0.2 | 1.1818 | 0 | Compute - Live | N | DAL13-101 | 3392 | 5566 | 0 | 0 | 8.958 | 0.24211 | 9.2001 |  | 0.79989 | 3.3039 | - | 0 | -
dal13.sr01.rk05 | DAL13 | 1 | 5 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108417 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 28 | 33 | 6 | 0 | 6 | 1 | 35 | 40 | 50 | 33 | 6 | 1 | 40 | 0 | 17 | 10 | 16 | 17 | 0 | 0.2 | 1.4545 | 0 | Compute - Live | N | DAL13-101 | 4724 | 4190 | 0 | 0 | 8.914 | 0.27012 | 10.8048 |  | -0.80485 | -2.9796 | - | 0 | -
dal13.sr01.rk06 | DAL13 | 1 | 6 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108419 | 5 | 1 | L1 | Z1-375 | 1 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk07 | DAL13 | 1 | 7 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108421 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 27 | 32 | 1 | 0 | 1 | 1 | 29 | 34 | 50 | 32 | 1 | 1 | 34 | 0 | 18 | 16 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Compute - Live | N | DAL13-101 | 3552 | 4453 | 0 | 0 | 8.005 | 0.25016 | 8.5053 |  | 1.4947 | 5.975 | - | 0 | -
dal13.sr01.rk08 | DAL13 | 1 | 8 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108423 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 34 | 39 | 0 | 0 | 0 | 1 | 35 | 40 | 50 | 39 | 0 | 1 | 40 | 0 | 11 | 10 | 10 | 11 | 0 | 0.2 | 0.90909 | 0 | Compute - Live | N | DAL13-101 | 3645 | 5348 | 0 | 0 | 8.993 | 0.23059 | 9.2236 |  | 0.77641 | 3.3671 | - | 0 | -
dal13.sr01.rk09 | DAL13 | 1 | 9 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108425 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 34 | 39 | 0 | 0 | 0 | 2 | 36 | 41 | 50 | 39 | 0 | 2 | 41 | 0 | 11 | 9 | 9 | 11 | 0 | 0.2 | 0.81818 | 0 | Compute - Live | N | DAL13-101 | 4709 | 4506 | 0 | 0 | 9.215 | 0.23628 | 9.6876 |  | 0.31244 | 1.3223 | - | 0 | -
dal13.sr01.rk10 | DAL13 | 1 | 10 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108427 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 37 | 42 | 3 | 0 | 3 | 1 | 41 | 46 | 50 | 42 | 3 | 1 | 46 | 0 | 8 | 4 | 7 | 8 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-101 | 5305 | 4754 | 0 | 0 | 10.059 | 0.2395 | 11.017 |  | -1.017 | -4.2463 | - | 0 | -
dal13.sr01.rk11 | DAL13 | 1 | 11 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108429 | 10 | 1 | L1 | Z1-375 | 1 |  |  | 34 | 39 | 2 | 0 | 2 | 1 | 37 | 42 | 50 | 39 | 2 | 1 | 42 | 0 | 11 | 8 | 10 | 11 | 0 | 0.2 | 0.90909 | 0 | Compute - Live | N | DAL13-101 | 3349 | 5813 | 0 | 0 | 9.162 | 0.23492 | 9.8668 |  | 0.13323 | 0.56713 | E | 0 | -
dal13.sr01.rk12 | DAL13 | 1 | 12 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108431 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 20 | 25 | 1 | 0 | 1 | 1 | 22 | 27 | 50 | 25 | 1 | 1 | 27 | 0 | 25 | 23 | 24 | 25 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1908 | 2052 | 0 | 0 | 3.96 | 0.1584 | 4.2768 |  | 1.7232 | 10.8788 | S | 0 | -
dal13.sr01.rk13 | DAL13 | 1 | 13 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108433 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 29 | 34 | 1 | 0 | 1 | 1 | 31 | 36 | 50 | 35 | 1 | 1 | 37 | 0 | 15 | 13 | 14 | 15 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2894 | 2777 | 0 | 0 | 5.671 | 0.16203 | 5.9951 |  | 0.0049429 | 0.030506 | - | 0 | -
dal13.sr01.rk14 | DAL13 | 1 | 14 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108435 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 22 | 27 | 0 | 0 | 0 | 0 | 22 | 27 | 50 | 31 | 0 | 0 | 31 | 0 | 19 | 19 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 2542 | 1679 | 0 | 0 | 4.221 | 0.13616 | 4.221 |  | 1.779 | 13.0654 | - | 0 | -
dal13.sr01.rk15 | DAL13 | 1 | 15 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108437 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 21 | 26 | 1 | 0 | 1 | 2 | 24 | 29 | 50 | 29 | 1 | 2 | 32 | 0 | 21 | 18 | 19 | 21 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 2814 | 2512 | 0 | 0 | 5.326 | 0.18366 | 5.877 |  | 0.12303 | 0.66992 | - | 0 | -
dal13.sr01.rk16 | DAL13 | 1 | 16 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108439 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 25 | 30 | 0 | 0 | 0 | 1 | 26 | 31 | 50 | 34 | 0 | 1 | 35 | 0 | 16 | 15 | 15 | 16 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2815 | 2554 | 0 | 0 | 5.369 | 0.15791 | 5.5269 |  | 0.47309 | 2.9959 | - | 0 | -
dal13.sr01.rk17 | DAL13 | 1 | 17 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108441 | 5 | 1 | L1 | Z1-375 | 2 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk18 | DAL13 | 1 | 18 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108443 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 28 | 33 | 2 | 0 | 2 | 0 | 30 | 35 | 50 | 38 | 3 | 0 | 41 | 0 | 12 | 9 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 3285 | 2788 | 0 | 0 | 6.073 | 0.15982 | 6.5524 |  | -0.55245 | -3.4568 | - | 0 | -
dal13.sr01.rk19 | DAL13 | 1 | 19 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108445 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 14 | 19 | 3 | 0 | 3 | 0 | 17 | 22 | 50 | 28 | 5 | 0 | 33 | 0 | 22 | 17 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 1371 | 1817 | 0 | 0 | 3.188 | 0.11386 | 3.7573 |  | 2.2427 | 19.6976 | - | 0 | -
dal13.sr01.rk20 | DAL13 | 1 | 20 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108447 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 16 | 21 | 7 | 0 | 7 | 0 | 23 | 28 | 50 | 26 | 14 | 0 | 40 | 0 | 24 | 10 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1870 | 2451 | 0 | 0 | 4.321 | 0.16619 | 6.6477 |  | -0.64769 | -3.8972 | - | 0 | -
dal13.sr01.rk21 | DAL13 | 1 | 21 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108449 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 15 | 20 | 6 | 0 | 6 | 0 | 21 | 26 | 50 | 26 | 10 | 0 | 36 | 0 | 24 | 14 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1948 | 1927 | 0 | 0 | 3.875 | 0.14904 | 5.3654 |  | 0.63462 | 4.2581 | - | 0 | -
dal13.sr01.rk22 | DAL13 | 1 | 22 | 1 | 10G | Dual Path | Sellable | Bare Metal | COD | Live | 50 | 1108451 | 6 | 1 | L1 | Z1-375 | 2 |  |  | 1 | 11 | 1 | 0 | 1 | 2 | 1 | 14 | 50 | 14 | 1 | 3 | 18 | 0 | 36 | 32 | 33 | 36 | 0 | 0.12 | 3 | 0 | Bare Metal - Live | N | DAL13-101 | 709 | 728 | 0 | 0 | 1.437 | 0.10264 | 1.8476 |  | 4.1524 | 40.4551 | E | 0 | -
dal13.sr01.rk23 | DAL13 | 1 | 23 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108453 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 19 | 24 | 5 | 0 | 5 | 0 | 24 | 29 | 50 | 30 | 9 | 0 | 39 | 0 | 20 | 11 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 2653 | 2587 | 0 | 0 | 5.24 | 0.17467 | 6.812 |  | -0.812 | -4.6489 | S | 0 | -
dal13.sr01.rk24 | DAL13 | 1 | 24 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108455 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 23 | 28 | 3 | 0 | 3 | 0 | 26 | 31 | 50 | 34 | 4 | 0 | 38 | 0 | 16 | 12 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 3195 | 3156 | 0 | 0 | 6.351 | 0.18679 | 7.0982 |  | -1.0982 | -5.8791 | - | 0 | -
dal13.sr01.rk25 | DAL13 | 1 | 25 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108457 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 24 | 29 | 4 | 0 | 4 | 2 | 30 | 35 | 50 | 34 | 4 | 5 | 43 | 0 | 16 | 7 | 11 | 16 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 3371 | 3336 | 0 | 0 | 6.707 | 0.19726 | 8.4824 |  | -2.4824 | -12.584 | - | 0 | -
dal13.sr01.rk26 | DAL13 | 1 | 26 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108459 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 25 | 30 | 3 | 0 | 3 | 2 | 30 | 35 | 50 | 34 | 5 | 3 | 42 | 0 | 16 | 8 | 13 | 16 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3035 | 3011 | 0 | 0 | 6.046 | 0.17782 | 7.4686 |  | -1.4686 | -8.2587 | - | 0 | -
dal13.sr01.rk27 | DAL13 | 1 | 27 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108461 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 26 | 31 | 1 | 0 | 1 | 1 | 28 | 33 | 50 | 36 | 1 | 1 | 38 | 0 | 14 | 12 | 13 | 14 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3193 | 3157 | 0 | 0 | 6.35 | 0.17639 | 6.7028 |  | -0.70278 | -3.9843 | - | 0 | -
dal13.sr01.rk28 | DAL13 | 1 | 28 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108463 | 5 | 1 | L1 | Z1-375 | 3 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk29 | DAL13 | 1 | 29 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108465 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 19 | 24 | 5 | 0 | 5 | 0 | 24 | 29 | 50 | 31 | 8 | 0 | 39 | 0 | 19 | 11 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 3074 | 2875 | 0 | 0 | 5.949 | 0.1919 | 7.4842 |  | -1.4842 | -7.7342 | - | 0 | -
dal13.sr01.rk30 | DAL13 | 1 | 30 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108467 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 29 | 34 | 3 | 0 | 3 | 2 | 34 | 39 | 50 | 36 | 4 | 5 | 45 | 0 | 14 | 5 | 9 | 14 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-102 | 3916 | 3873 | 0 | 0 | 7.789 | 0.21636 | 9.7363 |  | -3.7363 | -17.2686 | - | 0 | -
dal13.sr01.rk31 | DAL13 | 1 | 31 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108469 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 26 | 31 | 2 | 0 | 2 | 1 | 29 | 34 | 50 | 38 | 2 | 1 | 41 | 0 | 12 | 9 | 11 | 12 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 3898 | 3843 | 0 | 0 | 7.741 | 0.20371 | 8.3521 |  | -2.3521 | -11.5464 | - | 0 | -
dal13.sr01.rk32 | DAL13 | 1 | 32 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108471 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 24 | 29 | 1 | 0 | 1 | 2 | 27 | 32 | 50 | 32 | 2 | 9 | 43 | 0 | 18 | 7 | 9 | 18 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-102 | 3853 | 3331 | 0 | 0 | 7.184 | 0.2245 | 9.6535 |  | -3.6535 | -16.2739 | - | 0 | -
dal13.sr01.rk33 | DAL13 | 1 | 33 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108473 | 6 | 1 | L1 | Z1-375 | 3 |  |  | 18 | 23 | 3 | 0 | 3 | 1 | 22 | 27 | 50 | 26 | 7 | 2 | 35 | 0 | 24 | 15 | 22 | 24 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-102 | 3211 | 3222 | 0 | 0 | 6.433 | 0.24742 | 8.6598 |  | -2.6598 | -10.75 | E | 0 | -
dal13.sr01.rk34 | DAL13 | 1 | 34 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108475 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 21 | 26 | 0 | 0 | 0 | 0 | 21 | 26 | 50 | 33 | 0 | 0 | 33 | 0 | 17 | 17 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2905 | 2305 | 0 | 0 | 5.21 | 0.15788 | 5.21 |  | 0.79 | 5.0038 | S | 0 | -
dal13.sr01.rk35 | DAL13 | 1 | 35 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108477 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 20 | 25 | 2 | 0 | 2 | 0 | 22 | 27 | 50 | 27 | 2 | 0 | 29 | 0 | 23 | 21 | 23 | 23 | 0 | 0.12 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2105 | 2244 | 0 | 0 | 4.349 | 0.16107 | 4.6711 |  | 1.3289 | 8.2499 | - | 0 | -
dal13.sr01.rk36 | DAL13 | 1 | 36 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108479 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 23 | 28 | 0 | 0 | 0 | 0 | 23 | 28 | 50 | 33 | 0 | 0 | 33 | 0 | 17 | 17 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2623 | 2776 | 0 | 0 | 5.399 | 0.16361 | 5.399 |  | 0.601 | 3.6735 | - | 0 | -
dal13.sr01.rk37 | DAL13 | 1 | 37 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108481 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 22 | 27 | 1 | 0 | 1 | 1 | 24 | 29 | 50 | 31 | 1 | 1 | 33 | 0 | 19 | 17 | 18 | 19 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2242 | 1652 | 0 | 0 | 3.894 | 0.12561 | 4.1452 |  | 1.8548 | 14.7658 | - | 0 | -
dal13.sr01.rk38 | DAL13 | 1 | 38 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108483 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 18 | 23 | 1 | 0 | 1 | 2 | 21 | 26 | 50 | 29 | 1 | 3 | 33 | 0 | 21 | 17 | 18 | 21 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2271 | 2060 | 0 | 0 | 4.331 | 0.14934 | 4.9284 |  | 1.0716 | 7.1755 | - | 0 | -
dal13.sr01.rk39 | DAL13 | 1 | 39 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108485 | 5 | 1 | L1 | Z1-375 | 4 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk40 | DAL13 | 1 | 40 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108487 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 24 | 29 | 0 | 0 | 0 | 0 | 24 | 29 | 50 | 32 | 0 | 0 | 32 | 0 | 18 | 18 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2312 | 1987 | 0 | 0 | 4.299 | 0.13434 | 4.299 |  | 1.701 | 12.6615 | - | 0 | -
dal13.sr01.rk41 | DAL13 | 1 | 41 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108489 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 24 | 29 | 2 | 0 | 2 | 0 | 26 | 31 | 50 | 32 | 3 | 0 | 35 | 0 | 18 | 15 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2967 | 2990 | 0 | 0 | 5.957 | 0.18616 | 6.5155 |  | -0.51547 | -2.769 | - | 0 | -
dal13.sr01.rk42 | DAL13 | 1 | 42 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108491 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 18 | 23 | 0 | 0 | 0 | 0 | 18 | 23 | 50 | 23 | 0 | 0 | 23 | 0 | 27 | 27 | 27 | 27 | 0 | 0.12 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 1545 | 1669 | 0 | 0 | 3.214 | 0.13974 | 3.214 |  | 2.786 | 19.9371 | - | 0 | -
dal13.sr01.rk43 | DAL13 | 1 | 43 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108493 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 23 | 28 | 4 | 0 | 4 | 0 | 27 | 32 | 50 | 30 | 7 | 0 | 37 | 0 | 20 | 13 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 2014 | 1994 | 0 | 0 | 4.008 | 0.1336 | 4.9432 |  | 1.0568 | 7.9102 | - | 0 | -
dal13.sr01.rk44 | DAL13 | 1 | 44 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108495 | 6 | 1 | L1 | Z1-375 | 4 |  |  | 25 | 30 | 6 | 0 | 6 | 0 | 31 | 36 | 50 | 33 | 7 | 0 | 40 | 0 | 17 | 10 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2519 | 2464 | 0 | 0 | 4.983 | 0.151 | 6.04 |  | -0.04 | -0.2649 | E | 0 | -
dal13.sr01.rk45 | DAL13 | 1 | 45 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108297 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 15 | 20 | 7 | 0 | 7 | 2 | 24 | 29 | 50 | 28 | 11 | 3 | 42 | 0 | 22 | 8 | 19 | 22 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 1435 | 1880 | 0 | 0 | 3.315 | 0.11839 | 4.9725 |  | 1.0275 | 8.6787 | S | 0 | -
dal13.sr01.rk46 | DAL13 | 1 | 46 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108299 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 15 | 20 | 7 | 0 | 7 | 2 | 24 | 29 | 50 | 22 | 14 | 6 | 42 | 0 | 28 | 8 | 22 | 28 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2047 | 2271 | 0 | 0 | 4.318 | 0.19627 | 8.2435 |  | -2.2435 | -11.4303 | - | 0 | -
dal13.sr01.rk47 | DAL13 | 1 | 47 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108301 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 13 | 18 | 5 | 0 | 5 | 1 | 19 | 24 | 50 | 28 | 9 | 1 | 38 | 0 | 22 | 12 | 21 | 22 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 1964 | 2246 | 0 | 0 | 4.21 | 0.15036 | 5.7136 |  | 0.28643 | 1.905 | - | 0 | -
dal13.sr01.rk48 | DAL13 | 1 | 48 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108303 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 12 | 17 | 6 | 0 | 6 | 0 | 18 | 23 | 50 | 23 | 15 | 0 | 38 | 0 | 27 | 12 | 27 | 27 | 0 | 0.12 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 1595 | 1210 | 0 | 0 | 2.805 | 0.12196 | 4.6343 |  | 1.3657 | 11.1979 | - | 0 | -
dal13.sr01.rk49 | DAL13 | 1 | 49 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108305 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 11 | 16 | 7 | 0 | 7 | 1 | 19 | 24 | 50 | 27 | 13 | 1 | 41 | 0 | 23 | 9 | 22 | 23 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2145 | 1630 | 0 | 0 | 3.775 | 0.13981 | 5.7324 |  | 0.26759 | 1.9139 | - | 0 | -
dal13.sr01.rk50 | DAL13 | 1 | 50 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108307 | 5 | 1 | L1 | Z2-375 | 5 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk51 | DAL13 | 1 | 51 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108309 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 12 | 17 | 2 | 0 | 2 | 3 | 17 | 22 | 50 | 25 | 4 | 7 | 36 | 0 | 25 | 14 | 18 | 25 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 1325 | 1525 | 0 | 0 | 2.85 | 0.114 | 4.104 |  | 1.896 | 16.6316 | - | 0 | -
dal13.sr01.rk52 | DAL13 | 1 | 52 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108311 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 13 | 18 | 6 | 0 | 6 | 0 | 19 | 24 | 50 | 25 | 12 | 0 | 37 | 0 | 25 | 13 | 25 | 25 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 1429 | 1499 | 0 | 0 | 2.928 | 0.11712 | 4.3334 |  | 1.6666 | 14.2295 | - | 0 | -
dal13.sr01.rk53 | DAL13 | 1 | 53 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108313 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 13 | 18 | 4 | 0 | 4 | 0 | 17 | 22 | 50 | 29 | 8 | 0 | 37 | 0 | 21 | 13 | 21 | 21 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 1753 | 1349 | 0 | 0 | 3.102 | 0.10697 | 3.9577 |  | 2.0423 | 19.0928 | - | 0 | -
dal13.sr01.rk54 | DAL13 | 1 | 54 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108315 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 14 | 19 | 6 | 0 | 6 | 0 | 20 | 25 | 50 | 27 | 9 | 0 | 36 | 0 | 23 | 14 | 23 | 23 | 0 | 0.12 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 1836 | 1791 | 0 | 0 | 3.627 | 0.13433 | 4.836 |  | 1.164 | 8.665 | - | 0 | -
dal13.sr01.rk55 | DAL13 | 1 | 55 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108317 | 6 | 1 | L1 | Z2-375 | 5 |  |  | 15 | 20 | 4 | 0 | 4 | 2 | 21 | 26 | 50 | 27 | 7 | 2 | 36 | 0 | 23 | 14 | 21 | 23 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 1514 | 1772 | 0 | 0 | 3.286 | 0.1217 | 4.3813 |  | 1.6187 | 13.3001 | E | 0 | -
dal13.sr01.rk56 | DAL13 | 1 | 56 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108319 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 15 | 20 | 2 | 0 | 2 | 1 | 18 | 23 | 50 | 37 | 6 | 2 | 45 | 0 | 13 | 5 | 11 | 13 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 2452 | 2186 | 0 | 0 | 4.638 | 0.12535 | 5.6408 |  | 0.35919 | 2.8655 | S | 0 | -
dal13.sr01.rk57 | DAL13 | 1 | 57 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108321 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 14 | 19 | 1 | 0 | 1 | 2 | 17 | 22 | 50 | 35 | 2 | 10 | 47 | 0 | 15 | 3 | 5 | 15 | 0 | 0.12 | 0.45455 | 0 | Bare Metal - Live | N | DAL13-101 | 2703 | 1621 | 0 | 0 | 4.324 | 0.12354 | 5.8065 |  | 0.19349 | 1.5661 | - | 0 | -
dal13.sr01.rk58 | DAL13 | 1 | 58 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108323 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 12 | 17 | 4 | 0 | 4 | 0 | 16 | 21 | 50 | 33 | 12 | 0 | 45 | 0 | 17 | 5 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2073 | 2280 | 0 | 0 | 4.353 | 0.13191 | 5.9359 |  | 0.064091 | 0.48587 | - | 0 | -
dal13.sr01.rk59 | DAL13 | 1 | 59 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108325 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 22 | 27 | 2 | 0 | 2 | 1 | 25 | 30 | 50 | 34 | 3 | 4 | 41 | 0 | 16 | 9 | 12 | 16 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 3149 | 3035 | 0 | 0 | 6.184 | 0.18188 | 7.4572 |  | -1.4572 | -8.0116 | - | 0 | -
dal13.sr01.rk60 | DAL13 | 1 | 60 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108327 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 21 | 26 | 2 | 0 | 2 | 0 | 23 | 28 | 50 | 34 | 4 | 0 | 38 | 0 | 16 | 12 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2311 | 2653 | 0 | 0 | 4.964 | 0.146 | 5.548 |  | 0.452 | 3.0959 | - | 0 | -
dal13.sr01.rk61 | DAL13 | 1 | 61 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108329 | 5 | 1 | L1 | Z2-375 | 6 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk62 | DAL13 | 1 | 62 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108331 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 18 | 23 | 1 | 0 | 1 | 1 | 20 | 25 | 50 | 27 | 2 | 2 | 31 | 0 | 23 | 19 | 21 | 23 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 2207 | 2156 | 0 | 0 | 4.363 | 0.16159 | 5.0094 |  | 0.99063 | 6.1304 | - | 0 | -
dal13.sr01.rk63 | DAL13 | 1 | 63 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108333 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 10 | 15 | 4 | 0 | 4 | 0 | 14 | 19 | 50 | 23 | 8 | 0 | 31 | 0 | 27 | 19 | 27 | 27 | 0 | 0.12 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 1838 | 1837 | 0 | 0 | 3.675 | 0.15978 | 4.9533 |  | 1.0467 | 6.551 | - | 0 | -
dal13.sr01.rk64 | DAL13 | 1 | 64 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108335 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 16 | 21 | 4 | 0 | 4 | 0 | 20 | 25 | 50 | 34 | 6 | 0 | 40 | 0 | 16 | 10 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2305 | 2327 | 0 | 0 | 4.632 | 0.13624 | 5.4494 |  | 0.55059 | 4.0415 | - | 0 | -
dal13.sr01.rk65 | DAL13 | 1 | 65 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108337 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 15 | 20 | 6 | 0 | 6 | 1 | 22 | 27 | 50 | 24 | 13 | 2 | 39 | 0 | 26 | 11 | 24 | 26 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1658 | 1420 | 0 | 0 | 3.078 | 0.12825 | 5.0018 |  | 0.99825 | 7.7836 | - | 0 | -
dal13.sr01.rk66 | DAL13 | 1 | 66 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108339 | 6 | 1 | L1 | Z2-375 | 6 |  |  | 29 | 34 | 4 | 0 | 4 | 2 | 35 | 40 | 50 | 34 | 8 | 2 | 44 | 0 | 16 | 6 | 14 | 16 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2694 | 4745 | 0 | 0 | 7.439 | 0.21879 | 9.6269 |  | -3.6269 | -16.577 | E | 0 | -
dal13.sr01.rk67 | DAL13 | 1 | 67 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108341 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 13 | 18 | 13 | 0 | 13 | 2 | 28 | 33 | 50 | 23 | 14 | 3 | 40 | 0 | 27 | 10 | 24 | 27 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1796 | 1601 | 0 | 0 | 3.397 | 0.1477 | 5.9078 |  | 0.092174 | 0.62408 | S | 0 | -
dal13.sr01.rk68 | DAL13 | 1 | 68 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108343 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 25 | 30 | 3 | 0 | 3 | 0 | 28 | 33 | 50 | 33 | 4 | 0 | 37 | 0 | 17 | 13 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 3088 | 3031 | 0 | 0 | 6.119 | 0.18542 | 6.8607 |  | -0.8607 | -4.6418 | - | 0 | -
dal13.sr01.rk69 | DAL13 | 1 | 69 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108345 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 30 | 35 | 4 | 0 | 4 | 0 | 34 | 39 | 50 | 37 | 6 | 0 | 43 | 0 | 13 | 7 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 4062 | 3925 | 0 | 0 | 7.987 | 0.21586 | 9.2822 |  | -3.2822 | -15.2048 | - | 0 | -
dal13.sr01.rk70 | DAL13 | 1 | 70 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108347 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 22 | 27 | 4 | 0 | 4 | 1 | 27 | 32 | 50 | 36 | 7 | 1 | 44 | 0 | 14 | 6 | 13 | 14 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 3576 | 3438 | 0 | 0 | 7.014 | 0.19483 | 8.5727 |  | -2.5727 | -13.2044 | - | 0 | -
dal13.sr01.rk71 | DAL13 | 1 | 71 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108349 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 17 | 22 | 6 | 0 | 6 | 0 | 23 | 28 | 50 | 28 | 9 | 0 | 37 | 0 | 22 | 13 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 1866 | 1776 | 0 | 0 | 3.642 | 0.13007 | 4.8126 |  | 1.1874 | 9.1285 | - | 0 | -
dal13.sr01.rk72 | DAL13 | 1 | 72 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108351 | 5 | 1 | L1 | Z3-375 | 7 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk73 | DAL13 | 1 | 73 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108353 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 18 | 23 | 2 | 0 | 2 | 2 | 22 | 27 | 50 | 27 | 3 | 4 | 34 | 0 | 23 | 16 | 19 | 23 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 1929 | 1827 | 0 | 0 | 3.756 | 0.13911 | 4.7298 |  | 1.2702 | 9.131 | - | 0 | -
dal13.sr01.rk74 | DAL13 | 1 | 74 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108355 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 23 | 28 | 2 | 0 | 2 | 0 | 25 | 30 | 50 | 36 | 2 | 0 | 38 | 0 | 14 | 12 | 14 | 14 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2096 | 2472 | 0 | 0 | 4.568 | 0.12689 | 4.8218 |  | 1.1782 | 9.2855 | - | 0 | -
dal13.sr01.rk75 | DAL13 | 1 | 75 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108357 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 21 | 26 | 2 | 0 | 2 | 1 | 24 | 29 | 50 | 31 | 4 | 1 | 36 | 0 | 19 | 14 | 18 | 19 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2329 | 2419 | 0 | 0 | 4.748 | 0.15316 | 5.5138 |  | 0.48619 | 3.1744 | - | 0 | -
dal13.sr01.rk76 | DAL13 | 1 | 76 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108359 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 31 | 36 | 0 | 0 | 0 | 0 | 31 | 36 | 50 | 38 | 0 | 0 | 38 | 0 | 12 | 12 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2931 | 3372 | 0 | 0 | 6.303 | 0.16587 | 6.303 |  | -0.303 | -1.8267 | - | 0 | -
dal13.sr01.rk77 | DAL13 | 1 | 77 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108361 | 6 | 1 | L1 | Z3-375 | 7 |  |  | 31 | 36 | 2 | 0 | 2 | 0 | 33 | 38 | 50 | 40 | 2 | 0 | 42 | 0 | 10 | 8 | 10 | 10 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-101 | 4202 | 4126 | 0 | 0 | 8.328 | 0.2082 | 8.7444 |  | -2.7444 | -13.1816 | E | 0 | -
dal13.sr01.rk78 | DAL13 | 1 | 78 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108363 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 18 | 23 | 0 | 0 | 0 | 0 | 18 | 23 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2202 | 2248 | 0 | 0 | 4.45 | 0.15893 | 4.45 |  | 1.55 | 9.7528 | S | 0 | -
dal13.sr01.rk79 | DAL13 | 1 | 79 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108365 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 18 | 23 | 3 | 0 | 3 | 1 | 22 | 27 | 50 | 32 | 5 | 1 | 38 | 0 | 18 | 12 | 17 | 18 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2592 | 2264 | 0 | 0 | 4.856 | 0.15175 | 5.7665 |  | 0.2335 | 1.5387 | - | 0 | -
dal13.sr01.rk80 | DAL13 | 1 | 80 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108367 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 16 | 21 | 1 | 0 | 1 | 1 | 18 | 23 | 50 | 28 | 2 | 2 | 32 | 0 | 22 | 18 | 20 | 22 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 1650 | 2129 | 0 | 0 | 3.779 | 0.13496 | 4.3189 |  | 1.6811 | 12.4562 | - | 0 | -
dal13.sr01.rk81 | DAL13 | 1 | 81 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108369 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 20 | 25 | 1 | 0 | 1 | 1 | 22 | 27 | 50 | 30 | 2 | 1 | 33 | 0 | 20 | 17 | 19 | 20 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 2018 | 1854 | 0 | 0 | 3.872 | 0.12907 | 4.2592 |  | 1.7408 | 13.4876 | - | 0 | -
dal13.sr01.rk82 | DAL13 | 1 | 82 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108371 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 19 | 24 | 1 | 0 | 1 | 0 | 20 | 25 | 50 | 31 | 2 | 0 | 33 | 0 | 19 | 17 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 1916 | 1552 | 0 | 0 | 3.468 | 0.11187 | 3.6917 |  | 2.3083 | 20.6332 | - | 0 | -
dal13.sr01.rk83 | DAL13 | 1 | 83 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108373 | 5 | 1 | L1 | Z2-375 | 8 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk84 | DAL13 | 1 | 84 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108375 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 21 | 26 | 2 | 0 | 2 | 1 | 24 | 29 | 50 | 36 | 4 | 1 | 41 | 0 | 14 | 9 | 13 | 14 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2637 | 2572 | 0 | 0 | 5.209 | 0.14469 | 5.9325 |  | 0.067528 | 0.46669 | - | 0 | -
dal13.sr01.rk85 | DAL13 | 1 | 85 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108377 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 22 | 27 | 0 | 0 | 0 | 3 | 25 | 30 | 50 | 31 | 0 | 5 | 36 | 0 | 19 | 14 | 14 | 19 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 3175 | 3032 | 0 | 0 | 6.207 | 0.20023 | 7.2081 |  | -1.2081 | -6.0338 | - | 0 | -
dal13.sr01.rk86 | DAL13 | 1 | 86 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108379 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 32 | 37 | 2 | 0 | 2 | 0 | 34 | 39 | 50 | 41 | 2 | 0 | 43 | 0 | 9 | 7 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 4471 | 4494 | 0 | 0 | 8.965 | 0.21866 | 9.4023 |  | -3.4023 | -15.56 | - | 0 | -
dal13.sr01.rk87 | DAL13 | 1 | 87 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108381 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 17 | 22 | 0 | 0 | 0 | 3 | 20 | 25 | 50 | 28 | 0 | 4 | 32 | 0 | 22 | 18 | 18 | 22 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2601 | 2866 | 0 | 0 | 5.467 | 0.19525 | 6.248 |  | -0.248 | -1.2702 | - | 0 | -
dal13.sr01.rk88 | DAL13 | 1 | 88 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108383 | 6 | 1 | L1 | Z2-375 | 8 |  |  | 34 | 39 | 0 | 0 | 0 | 2 | 36 | 41 | 50 | 39 | 0 | 2 | 41 | 0 | 11 | 9 | 9 | 11 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3582 | 4270 | 0 | 0 | 7.852 | 0.20133 | 8.2547 |  | -2.2547 | -11.1987 | E | 0 | -
dal13.sr01.rk89 | DAL13 | 1 | 89 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108497 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | S | 1 | -
dal13.sr01.rk90 | DAL13 | 1 | 90 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108499 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 2 | -
dal13.sr01.rk91 | DAL13 | 1 | 91 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108501 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 50 | 6 | 0 | 10 | 16 | 0 | 44 | 34 | 34 | 44 | 0 | 0.12 | 3.0909 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk92 | DAL13 | 1 | 92 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108503 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 7 | 0 | 0 | 0 | 3 | 0 | 10 | 50 | 18 | 0 | 10 | 28 | 0 | 32 | 22 | 22 | 32 | 0 | 0.12 | 2 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk93 | DAL13 | 1 | 93 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108505 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 1 | -
dal13.sr01.rk94 | DAL13 | 1 | 94 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108507 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 1 | 4 | 0 | 4 | 0 | 0 | 5 | 50 | 1 | 20 | 0 | 21 | 0 | 49 | 29 | 49 | 49 | 0 | 0.12 | 4.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk95 | DAL13 | 1 | 95 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108509 | 6 | 1 | L1 | Z3-375 | 9 | vlam - vlam - 11/3/2021 - NG Block Racks |  | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 38 | 0 | 0 | 38 | 0 | 12 | 12 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk96 | DAL13 | 1 | 96 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108511 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 19 | 50 | 43 | 0 | 0 | 43 | 0 | 7 | 7 | 7 | 7 | 0 | 0.12 | 0.63636 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk97 | DAL13 | 1 | 97 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108513 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 1 | -
dal13.sr01.rk98 | DAL13 | 1 | 98 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108515 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 50 | 3 | 0 | 10 | 13 | 0 | 47 | 37 | 37 | 47 | 0 | 0.12 | 3.3636 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk99 | DAL13 | 1 | 99 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108517 | 6 | 1 | L1 | Z3-375 | 9 |  |  | 0 | 7 | 0 | 0 | 0 | 3 | 0 | 10 | 50 | 15 | 0 | 10 | 25 | 0 | 35 | 25 | 25 | 35 | 0 | 0.12 | 2.2727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | E | 0 | -
dal13.sr01.rk100 | DAL13 | 1 | 100 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108519 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 15 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | S | 0 | -
dal13.sr01.rk101 | DAL13 | 1 | 101 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108521 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 11 | 13 | 0 | 0 | 0 | 0 | 11 | 13 | 50 | 40 | 0 | 0 | 40 | 0 | 10 | 10 | 10 | 10 | 0 | 0.12 | 0.90909 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk102 | DAL13 | 1 | 102 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108523 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 9 | 12 | 0 | 0 | 0 | 0 | 9 | 12 | 50 | 39 | 0 | 0 | 39 | 0 | 11 | 11 | 11 | 11 | 0 | 0.12 | 1 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk103 | DAL13 | 1 | 103 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108525 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 11 | 14 | 0 | 0 | 0 | 0 | 11 | 14 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk104 | DAL13 | 1 | 104 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108527 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 13 | 15 | 0 | 0 | 0 | 0 | 13 | 15 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk105 | DAL13 | 1 | 105 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108529 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 14 | 16 | 0 | 0 | 0 | 0 | 14 | 16 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk106 | DAL13 | 1 | 106 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108531 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 13 | 14 | 0 | 0 | 0 | 0 | 13 | 14 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk107 | DAL13 | 1 | 107 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108533 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 11 | 14 | 0 | 0 | 0 | 0 | 11 | 14 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk108 | DAL13 | 1 | 108 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108535 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 9 | 12 | 0 | 0 | 0 | 0 | 9 | 12 | 50 | 39 | 0 | 0 | 39 | 0 | 11 | 11 | 11 | 11 | 0 | 0.12 | 1 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk109 | DAL13 | 1 | 109 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108537 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 11 | 13 | 0 | 0 | 0 | 0 | 11 | 13 | 50 | 40 | 0 | 0 | 40 | 0 | 10 | 10 | 10 | 10 | 0 | 0.12 | 0.90909 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk110 | DAL13 | 1 | 110 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108539 | 6 | 1 | L1 | Z2-375 | 10 |  |  | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 15 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | E | 0 | -
dal13.sr01.rk111 | DAL13 | 1 | 111 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108541 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 3 | 0 | 0 | 0 | 4 | 0 | 7 | 50 | 3 | 0 | 20 | 23 | 0 | 47 | 27 | 27 | 47 | 0 | 0.12 | 2.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | S | 0 | -
dal13.sr01.rk112 | DAL13 | 1 | 112 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108543 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.12 | 4.2727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk113 | DAL13 | 1 | 113 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108545 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk114 | DAL13 | 1 | 114 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108547 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 37 | 0 | 0 | 37 | 0 | 13 | 13 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk115 | DAL13 | 1 | 115 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108549 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 6 | 0 | 0 | 6 | 0 | 44 | 44 | 44 | 44 | 0 | 0.12 | 4 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk116 | DAL13 | 1 | 116 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108551 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 2 | 0 | 0 | 2 | 0 | 48 | 48 | 48 | 48 | 0 | 0.12 | 4.3636 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk117 | DAL13 | 1 | 117 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108553 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 36 | 0 | 0 | 36 | 0 | 14 | 14 | 14 | 14 | 0 | 0.12 | 1.2727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk118 | DAL13 | 1 | 118 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108555 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 23 | 0 | 0 | 23 | 0 | 27 | 27 | 27 | 27 | 0 | 0.12 | 2.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk119 | DAL13 | 1 | 119 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108557 | 6 | 1 | L1 | Z3-375 | 11 |  |  | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 23 | 0 | 0 | 23 | 0 | 27 | 27 | 27 | 27 | 0 | 0.12 | 2.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk120 | DAL13 | 1 | 120 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108559 | 6 | 1 | L1 | Z3-375 | 11 | vlam - vlam - 11/3/2021 - NG Block Racks |  | 0 | 10 | 6 | 0 | 6 | 1 | 0 | 17 | 50 | 20 | 16 | 1 | 37 | 0 | 30 | 13 | 29 | 30 | 0 | 0.12 | 2.6364 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk121 | DAL13 | 1 | 121 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108561 | 6 | 1 | L1 | Z3-375 | 11 | vlam - vlam - 11/3/2021 - NG File Racks |  | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 11 | 50 | 16 | 0 | 1 | 17 | 0 | 34 | 33 | 33 | 34 | 0 | 0.12 | 3 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | E | 0 | -
dal13.sr01.rk122 | DAL13 | 1 | 122 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108563 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 13 | 13 | 0 | 0 | 0 | 0 | 13 | 13 | 50 | 34 | 0 | 0 | 34 | 0 | 16 | 16 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | S | 0 | -
dal13.sr01.rk123 | DAL13 | 1 | 123 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108565 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 9 | 11 | 0 | 0 | 0 | 0 | 9 | 11 | 50 | 32 | 0 | 0 | 32 | 0 | 18 | 18 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk124 | DAL13 | 1 | 124 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108567 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 7 | 10 | 0 | 0 | 0 | 0 | 7 | 10 | 50 | 31 | 0 | 0 | 31 | 0 | 19 | 19 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk125 | DAL13 | 1 | 125 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108569 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 8 | 10 | 0 | 0 | 0 | 1 | 9 | 11 | 50 | 30 | 0 | 1 | 31 | 0 | 20 | 19 | 19 | 20 | 0 | 0.12 | 1.7273 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk126 | DAL13 | 1 | 126 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108571 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 11 | 12 | 0 | 0 | 0 | 0 | 11 | 12 | 50 | 32 | 0 | 0 | 32 | 0 | 18 | 18 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk127 | DAL13 | 1 | 127 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108573 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 12 | 14 | 0 | 0 | 0 | 0 | 12 | 14 | 50 | 34 | 0 | 0 | 34 | 0 | 16 | 16 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk128 | DAL13 | 1 | 128 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108575 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 11 | 13 | 0 | 0 | 0 | 0 | 11 | 13 | 50 | 33 | 0 | 0 | 33 | 0 | 17 | 17 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk129 | DAL13 | 1 | 129 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108577 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 8 | 9 | 0 | 0 | 0 | 0 | 8 | 9 | 50 | 29 | 0 | 0 | 29 | 0 | 21 | 21 | 21 | 21 | 0 | 0.12 | 1.9091 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk130 | DAL13 | 1 | 130 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108579 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 7 | 10 | 0 | 0 | 0 | 0 | 7 | 10 | 50 | 31 | 0 | 0 | 31 | 0 | 19 | 19 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk131 | DAL13 | 1 | 131 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108581 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 9 | 11 | 0 | 0 | 0 | 0 | 9 | 11 | 50 | 32 | 0 | 0 | 32 | 0 | 18 | 18 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk132 | DAL13 | 1 | 132 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1108583 | 6 | 1 | L1 | Z2-375 | 12 |  |  | 13 | 13 | 0 | 0 | 0 | 0 | 13 | 13 | 50 | 34 | 0 | 0 | 34 | 0 | 16 | 16 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | E | 0 | -
dal13.sr01.rk133 | DAL13 | 1 | 133 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108385 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 6 | 0 | 0 | 6 | 0 | 44 | 44 | 44 | 44 | 0 | 0.092 | 4 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | S | 0 | -
dal13.sr01.rk134 | DAL13 | 1 | 134 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108387 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 18 | 21 | 1 | 0 | 1 | 0 | 19 | 22 | 50 | 39 | 1 | 0 | 40 | 0 | 11 | 10 | 11 | 11 | 0 | 0.092 | 1 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk135 | DAL13 | 1 | 135 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108389 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 9 | 12 | 2 | 0 | 2 | 6 | 11 | 20 | 50 | 19 | 2 | 14 | 35 | 0 | 31 | 15 | 17 | 31 | 0 | 0.092 | 1.5455 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk136 | DAL13 | 1 | 136 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108391 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 18 | 21 | 1 | 0 | 1 | 0 | 19 | 22 | 50 | 37 | 1 | 0 | 38 | 0 | 13 | 12 | 13 | 13 | 0 | 0.092 | 1.1818 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk137 | DAL13 | 1 | 137 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108593 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 18 | 23 | 0 | 0 | 0 | 0 | 18 | 23 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.092 | 0.81818 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk138 | DAL13 | 1 | 138 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108595 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 21 | 25 | 3 | 0 | 3 | 0 | 24 | 28 | 50 | 32 | 6 | 0 | 38 | 0 | 18 | 12 | 18 | 18 | 0 | 0.092 | 1.6364 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk139 | DAL13 | 1 | 139 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108597 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 15 | 21 | 0 | 0 | 0 | 0 | 15 | 21 | 50 | 36 | 0 | 0 | 36 | 0 | 14 | 14 | 14 | 14 | 0 | 0.092 | 1.2727 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk140 | DAL13 | 1 | 140 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108599 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 23 | 25 | 2 | 0 | 2 | 0 | 25 | 27 | 50 | 40 | 3 | 0 | 43 | 0 | 10 | 7 | 10 | 10 | 0 | 0.092 | 0.90909 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk141 | DAL13 | 1 | 141 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108601 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 13 | 17 | 2 | 0 | 2 | 0 | 15 | 19 | 50 | 30 | 3 | 0 | 33 | 0 | 20 | 17 | 20 | 20 | 0 | 0.092 | 1.8182 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk142 | DAL13 | 1 | 142 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108603 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 22 | 24 | 0 | 0 | 0 | 0 | 22 | 24 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.092 | 0.72727 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk143 | DAL13 | 1 | 143 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108605 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 24 | 27 | 0 | 0 | 0 | 0 | 24 | 27 | 50 | 34 | 0 | 0 | 34 | 0 | 16 | 16 | 16 | 16 | 0 | 0.092 | 1.4545 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk144 | DAL13 | 1 | 144 | 1 | 10G | Dual Path | Unsellable | Fabric | DTS | Live | 50 | 1108607 | 4.6 | 1 | L1 | Z3-375 | 13 |  |  | 2 | 4 | 0 | 0 | 0 | 0 | 2 | 4 | 50 | 6 | 0 | 0 | 6 | 0 | 44 | 44 | 44 | 44 | 0 | 0.092 | 4 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | E | 0 | -
dal13.sr01.rk145 | DAL13 | 1 | 145 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3487641 | 20 | 1 | L1 | Z4-375 | 14 | ccoronado - Adding SL tag Phillip Huffman. Ticket: 154281873 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr01.rk146 | DAL13 | 1 | 146 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3487643 | 20 | 1 | L1 | Z4-375 | 14 | ccoronado - Adding SL tag Phillip Huffman. Ticket: 154281873 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk147 | DAL13 | 1 | 147 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3487645 | 20 | 1 | L1 | Z4-375 | 14 | ccoronado - Adding SL tag Phillip Huffman. Ticket: 154281873 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk148 | DAL13 | 1 | 148 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3467934 | 20 | 1 | L1 | Z4-375 | 14 | llarin - SL tag change per ticket:157582306 |  | 43 | 47 | 0 | 0 | 0 | 0 | 43 | 47 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk149 | DAL13 | 1 | 149 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3467936 | 20 | 1 | L1 | Z4-375 | 14 | llarin - SL tag change per ticket:157582306 |  | 43 | 47 | 0 | 0 | 0 | 0 | 43 | 47 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk150 | DAL13 | 1 | 150 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1108619 | 0 | 1 | L1 | Z4-375 | 14 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr01.rk151 | DAL13 | 1 | 151 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1108621 | 0 | 1 | L1 | Z4-375 | 14 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr01.rk152 | DAL13 | 1 | 152 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1108623 | 0 | 1 | L1 | Z4-375 | 14 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr01.rk153 | DAL13 | 1 | 153 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1108625 | 0 | 1 | L1 | Z4-375 | 14 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr01.rk154 | DAL13 | 1 | 154 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1108627 | 0 | 1 | L1 | Z4-375 | 14 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr01.rk155 | DAL13 | 1 | 155 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1108629 | 0 | 1 | L1 | Z4-375 | 14 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 6 | -
dal13.sr01.rk156 | DAL13 | 1 | 156 | 1 | 10G | Dual Path | Unsellable | Network | Fiber | Live | 50 | 1108631 | 0 | 1 | L1 | Z3-375 | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Network - Live | Y | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 0 | 0 | S | 1 | -
dal13.sr01.rk157 | DAL13 | 1 | 157 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108633 | 9.1 | 1 | L1 | Z3-375 | 15 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.182 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 9.1 | 0 | - | 0 | -
dal13.sr01.rk158 | DAL13 | 1 | 158 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108635 | 9.1 | 1 | L1 | Z3-375 | 15 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 26 | 0 | 0 | 26 | 0 | 24 | 24 | 24 | 24 | 0 | 0.182 | 2.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk159 | DAL13 | 1 | 159 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108637 | 9.1 | 1 | L1 | Z3-375 | 15 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.182 | 2.5455 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk160 | DAL13 | 1 | 160 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108639 | 9.1 | 1 | L1 | Z3-375 | 15 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.182 | 2.5455 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk161 | DAL13 | 1 | 161 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108641 | 9.1 | 1 | L1 | Z4-375 | 15 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.182 | 2.5455 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk162 | DAL13 | 1 | 162 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108643 | 9.1 | 1 | L1 | Z4-375 | 15 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 23 | 0 | 0 | 23 | 0 | 27 | 27 | 27 | 27 | 0 | 0.182 | 2.4545 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk163 | DAL13 | 1 | 163 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108645 | 9.1 | 1 | L1 | Z3-375 | 15 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 26 | 0 | 0 | 26 | 0 | 24 | 24 | 24 | 24 | 0 | 0.182 | 2.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk164 | DAL13 | 1 | 164 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108647 | 9.1 | 1 | L1 | Z4-375 | 15 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 26 | 0 | 0 | 26 | 0 | 24 | 24 | 24 | 24 | 0 | 0.182 | 2.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk165 | DAL13 | 1 | 165 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108649 | 9.1 | 1 | L1 | Z4-375 | 15 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.182 | 0.72727 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk166 | DAL13 | 1 | 166 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108651 | 9.1 | 1 | L1 | Z4-375 | 15 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.182 | 2 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr01.rk167 | DAL13 | 1 | 167 | 1 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1108653 | 9.1 | 1 | L1 | Z4-375 | 15 |  |  | 0 | 13 | 1 | 0 | 1 | 2 | 0 | 16 | 50 | 21 | 1 | 2 | 24 | 0 | 29 | 26 | 27 | 29 | 0 | 0.182 | 2.4545 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 9.1 | 0 | E | 0 | -
dal13.sr01.rk168 | DAL13 | 1 | 168 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108655 | 6 | 1 | L1 | Z4-375 | 16 | vlam - NetApp |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.12 | 4.2727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | S | 0 | -
dal13.sr01.rk169 | DAL13 | 1 | 169 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108657 | 6 | 1 | L1 | Z4-375 | 16 | vlam - NetApp |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.12 | 4.2727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk170 | DAL13 | 1 | 170 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108659 | 6 | 1 | L1 | Z4-375 | 16 | vlam - NetApp |  | 3 | 16 | 1 | 0 | 1 | 1 | 3 | 18 | 50 | 32 | 1 | 1 | 34 | 0 | 18 | 16 | 17 | 18 | 0 | 0.12 | 1.5455 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk171 | DAL13 | 1 | 171 | 1 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108661 | 6 | 1 | L1 | Z4-375 | 16 | vlam - NetApp |  | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 19 | 50 | 46 | 0 | 0 | 46 | 0 | 4 | 4 | 4 | 4 | 0 | 0.12 | 0.36364 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 0 | -
dal13.sr01.rk172 | DAL13 | 1 | 172 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108663 | 4.6 | 1 | L1 | Z4-375 | 16 |  |  | 15 | 16 | 3 | 0 | 3 | 0 | 18 | 19 | 50 | 25 | 6 | 0 | 31 | 0 | 25 | 19 | 25 | 25 | 0 | 0.092 | 2.2727 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk173 | DAL13 | 1 | 173 | 1 | 10G | Dual Path | Unsellable | Network | Network Spares | Live | 50 | 1108665 | 0 | 1 | L1 | Z4-375 | 16 |  |  | 0 | 5 | 8 | 0 | 8 | 10 | 0 | 23 | 50 | 5 | 10 | 11 | 26 | 0 | 45 | 24 | 34 | 45 | 0 | 0 | 3.0909 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 0 | 0 | - | 0 | -
dal13.sr01.rk174 | DAL13 | 1 | 174 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108667 | 4.6 | 1 | L1 | Z4-375 | 16 |  |  | 16 | 17 | 2 | 0 | 2 | 0 | 18 | 19 | 50 | 31 | 4 | 0 | 35 | 0 | 19 | 15 | 19 | 19 | 0 | 0.092 | 1.7273 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk175 | DAL13 | 1 | 175 | 1 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1108669 | 4.6 | 1 | L1 | Z4-375 | 16 |  |  | 19 | 20 | 1 | 0 | 1 | 0 | 20 | 21 | 50 | 38 | 2 | 0 | 40 | 0 | 12 | 10 | 12 | 12 | 0 | 0.092 | 1.0909 | 0 | Fabric - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr01.rk176 | DAL13 | 1 | 176 | 1 | 10G | Dual Path | Sellable | Network | Load Balancer | Live | 50 | 1108671 | 6 | 1 | L1 | Z4-375 | 16 |  |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 49 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 1 | -
dal13.sr01.rk177 | DAL13 | 1 | 177 | 1 | 10G | Dual Path | Sellable | Network | Firewall | Live | 50 | 1108673 | 6 | 1 | L1 | Z4-375 | 16 |  |  | 0 | 0 | 13 | 0 | 13 | 6 | 0 | 19 | 50 | 0 | 13 | 6 | 19 | 0 | 50 | 31 | 44 | 50 | 0 | 0.12 | 4 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | - | 2 | -
dal13.sr01.rk178 | DAL13 | 1 | 178 | 1 | 10G | Dual Path | Sellable | Network | Firewall | Live | 50 | 1108675 | 6 | 1 | L1 | Z4-375 | 16 |  |  | 0 | 0 | 4 | 0 | 4 | 3 | 0 | 7 | 50 | 0 | 4 | 3 | 7 | 0 | 50 | 43 | 47 | 50 | 0 | 0.12 | 4.2727 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 6 | 0 | E | 3 | -
dal13.sr01.rk179 | DAL13 | 1 | 179 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108585 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 28 | 33 | 4 | 0 | 4 | 0 | 32 | 37 | 50 | 33 | 4 | 0 | 37 | 0 | 17 | 13 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Compute - Live | N | DAL13-101 | 3884 | 3880 | 0 | 0 | 7.764 | 0.23527 | 8.7051 |  | 1.2949 | 5.5039 | S | 0 | -
dal13.sr01.rk180 | DAL13 | 1 | 180 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108587 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 29 | 34 | 0 | 0 | 0 | 4 | 33 | 38 | 50 | 34 | 0 | 4 | 38 | 0 | 16 | 12 | 12 | 16 | 0 | 0.2 | 1.0909 | 0 | Compute - Live | N | DAL13-101 | 3998 | 3777 | 0 | 0 | 7.775 | 0.22868 | 8.6897 |  | 1.3103 | 5.7299 | - | 0 | -
dal13.sr01.rk181 | DAL13 | 1 | 181 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108589 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 37 | 42 | 0 | 0 | 0 | 1 | 38 | 43 | 50 | 42 | 0 | 1 | 43 | 0 | 8 | 7 | 7 | 8 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-101 | 4540 | 5525 | 0 | 0 | 10.065 | 0.23964 | 10.3046 |  | -0.30464 | -1.2712 | - | 0 | -
dal13.sr01.rk182 | DAL13 | 1 | 182 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108591 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 34 | 39 | 0 | 0 | 0 | 2 | 36 | 41 | 50 | 39 | 0 | 2 | 41 | 0 | 11 | 9 | 9 | 11 | 0 | 0.2 | 0.81818 | 0 | Compute - Live | N | DAL13-101 | 4345 | 5167 | 0 | 0 | 9.512 | 0.2439 | 9.9998 |  | 0.00020513 | 0.00084104 | - | 0 | -
dal13.sr01.rk183 | DAL13 | 1 | 183 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108693 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 34 | 39 | 0 | 0 | 0 | 3 | 37 | 42 | 50 | 39 | 0 | 3 | 42 | 0 | 11 | 8 | 8 | 11 | 0 | 0.2 | 0.72727 | 0 | Compute - Live | N | DAL13-101 | 3858 | 5202 | 0 | 0 | 9.06 | 0.23231 | 9.7569 |  | 0.24308 | 1.0464 | - | 0 | -
dal13.sr01.rk184 | DAL13 | 1 | 184 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108695 | 5 | 1 | L1 | Z4-375 | 17 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk185 | DAL13 | 1 | 185 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108697 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 37 | 42 | 1 | 0 | 1 | 2 | 40 | 45 | 50 | 42 | 1 | 2 | 45 | 0 | 8 | 5 | 6 | 8 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-101 | 4270 | 5573 | 0 | 0 | 9.843 | 0.23436 | 10.5461 |  | -0.54607 | -2.3301 | - | 0 | -
dal13.sr01.rk186 | DAL13 | 1 | 186 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108699 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 31 | 36 | 1 | 0 | 1 | 1 | 33 | 38 | 50 | 36 | 1 | 1 | 38 | 0 | 14 | 12 | 13 | 14 | 0 | 0.2 | 1.1818 | 0 | Compute - Live | N | DAL13-101 | 5258 | 0 | 0 | 0 | 5.258 | 0.14606 | 5.5501 | ERROR | 4.4499 | 30.4671 | - | 0 | -
dal13.sr01.rk187 | DAL13 | 1 | 187 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108701 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 32 | 37 | 1 | 0 | 1 | 1 | 34 | 39 | 50 | 37 | 1 | 1 | 39 | 0 | 13 | 11 | 12 | 13 | 0 | 0.2 | 1.0909 | 0 | Compute - Live | N | DAL13-101 | 4161 | 4289 | 0 | 0 | 8.45 | 0.22838 | 8.9068 |  | 1.0932 | 4.787 | - | 0 | -
dal13.sr01.rk188 | DAL13 | 1 | 188 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108703 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 42 | 47 | 0 | 0 | 0 | 0 | 42 | 47 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-101 | 5491 | 5566 | 0 | 0 | 11.057 | 0.23526 | 11.057 |  | -1.057 | -4.493 | - | 0 | -
dal13.sr01.rk189 | DAL13 | 1 | 189 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1108705 | 10 | 1 | L1 | Z4-375 | 17 |  |  | 42 | 47 | 0 | 0 | 0 | 0 | 42 | 47 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-101 | 4869 | 5338 | 0 | 0 | 10.207 | 0.21717 | 10.207 |  | -0.207 | -0.95317 | E | 0 | -
dal13.sr01.rk190 | DAL13 | 1 | 190 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108707 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 8 | 13 | 4 | 0 | 4 | 1 | 13 | 18 | 50 | 13 | 6 | 8 | 27 | 0 | 37 | 23 | 29 | 37 | 0 | 0.12 | 2.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 1287 | 1191 | 0 | 0 | 2.478 | 0.19062 | 5.1466 |  | 0.85338 | 4.477 | S | 0 | -
dal13.sr01.rk191 | DAL13 | 1 | 191 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108709 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 13 | 18 | 1 | 0 | 1 | 0 | 14 | 19 | 50 | 25 | 1 | 0 | 26 | 0 | 25 | 24 | 25 | 25 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 1788 | 1618 | 0 | 0 | 3.406 | 0.13624 | 3.5422 |  | 2.4578 | 18.0399 | - | 0 | -
dal13.sr01.rk192 | DAL13 | 1 | 192 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108711 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 10 | 15 | 1 | 0 | 1 | 0 | 11 | 16 | 50 | 19 | 2 | 0 | 21 | 0 | 31 | 29 | 31 | 31 | 0 | 0.12 | 2.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 1142 | 1182 | 0 | 0 | 2.324 | 0.12232 | 2.5686 |  | 3.4314 | 28.0534 | - | 0 | -
dal13.sr01.rk193 | DAL13 | 1 | 193 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108713 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 8 | 13 | 3 | 0 | 3 | 3 | 14 | 19 | 50 | 18 | 5 | 6 | 29 | 0 | 32 | 21 | 26 | 32 | 0 | 0.12 | 2.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 1222 | 1804 | 0 | 0 | 3.026 | 0.16811 | 4.8752 |  | 1.1248 | 6.6907 | - | 0 | -
dal13.sr01.rk194 | DAL13 | 1 | 194 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108715 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 11 | 16 | 3 | 0 | 3 | 1 | 15 | 20 | 50 | 23 | 6 | 2 | 31 | 0 | 27 | 19 | 25 | 27 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 1901 | 2077 | 0 | 0 | 3.978 | 0.17296 | 5.3617 |  | 0.63835 | 3.6908 | - | 0 | -
dal13.sr01.rk195 | DAL13 | 1 | 195 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108717 | 5 | 1 | L1 | Z4-375 | 18 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk196 | DAL13 | 1 | 196 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108719 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 17 | 22 | 3 | 0 | 3 | 1 | 21 | 26 | 50 | 30 | 3 | 1 | 34 | 0 | 20 | 16 | 19 | 20 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 2088 | 2371 | 0 | 0 | 4.459 | 0.14863 | 5.0535 |  | 0.94647 | 6.3678 | - | 0 | -
dal13.sr01.rk197 | DAL13 | 1 | 197 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108721 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 18 | 23 | 8 | 0 | 8 | 0 | 26 | 31 | 50 | 26 | 14 | 0 | 40 | 0 | 24 | 10 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2743 | 2676 | 0 | 0 | 5.419 | 0.20842 | 8.3369 |  | -2.3369 | -11.2124 | - | 0 | -
dal13.sr01.rk198 | DAL13 | 1 | 198 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108723 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 19 | 24 | 2 | 0 | 2 | 0 | 21 | 26 | 50 | 34 | 3 | 0 | 37 | 0 | 16 | 13 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2837 | 2767 | 0 | 0 | 5.604 | 0.16482 | 6.0985 |  | -0.098471 | -0.59743 | - | 0 | -
dal13.sr01.rk199 | DAL13 | 1 | 199 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108725 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 16 | 21 | 6 | 0 | 6 | 0 | 22 | 27 | 50 | 24 | 9 | 0 | 33 | 0 | 26 | 17 | 26 | 26 | 0 | 0.12 | 2.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 1844 | 2074 | 0 | 0 | 3.918 | 0.16325 | 5.3872 |  | 0.61275 | 3.7534 | - | 0 | -
dal13.sr01.rk200 | DAL13 | 1 | 200 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108727 | 6 | 1 | L1 | Z4-375 | 18 |  |  | 22 | 27 | 0 | 0 | 0 | 1 | 23 | 28 | 50 | 38 | 0 | 2 | 40 | 0 | 12 | 10 | 10 | 12 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-101 | 3098 | 2740 | 0 | 0 | 5.838 | 0.15363 | 6.1453 |  | -0.14526 | -0.94553 | E | 0 | -
dal13.sr01.rk201 | DAL13 | 1 | 201 | 1 | 10G | Dual Path | Sellable | Network | Ded. Firewall | Live | 50 | 1108729 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 50 | 26 | 0 | 0 | 26 | 0 | 24 | 24 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Network - Live | N | DAL13-101 | 2126 | 2095 | 0 | 0 | 4.221 | 0.16235 | 4.221 |  | 1.779 | 10.9581 | S | 0 | -
dal13.sr01.rk202 | DAL13 | 1 | 202 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108731 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 20 | 25 | 3 | 0 | 3 | 0 | 23 | 28 | 50 | 30 | 3 | 0 | 33 | 0 | 20 | 17 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 2926 | 2911 | 0 | 0 | 5.837 | 0.19457 | 6.4207 |  | -0.4207 | -2.1622 | - | 0 | -
dal13.sr01.rk203 | DAL13 | 1 | 203 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108733 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 18 | 23 | 4 | 0 | 4 | 0 | 22 | 27 | 50 | 28 | 9 | 0 | 37 | 0 | 22 | 13 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 3899 | 3614 | 0 | 0 | 7.513 | 0.26832 | 9.9279 |  | -3.9279 | -14.6388 | - | 0 | -
dal13.sr01.rk204 | DAL13 | 1 | 204 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108735 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 17 | 22 | 6 | 0 | 6 | 0 | 23 | 28 | 50 | 25 | 14 | 0 | 39 | 0 | 25 | 11 | 25 | 25 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2172 | 2369 | 0 | 0 | 4.541 | 0.18164 | 7.084 |  | -1.084 | -5.9676 | - | 0 | -
dal13.sr01.rk205 | DAL13 | 1 | 205 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108737 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 18 | 23 | 3 | 0 | 3 | 2 | 23 | 28 | 50 | 28 | 4 | 5 | 37 | 0 | 22 | 13 | 17 | 22 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2363 | 2329 | 0 | 0 | 4.692 | 0.16757 | 6.2001 |  | -0.20014 | -1.1944 | - | 0 | -
dal13.sr01.rk206 | DAL13 | 1 | 206 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108739 | 5 | 1 | L1 | Z6-375 | 19 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk207 | DAL13 | 1 | 207 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108741 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 13 | 18 | 3 | 0 | 3 | 1 | 17 | 22 | 50 | 18 | 4 | 8 | 30 | 0 | 32 | 20 | 24 | 32 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2253 | 2214 | 0 | 0 | 4.467 | 0.24817 | 7.445 |  | -1.445 | -5.8227 | - | 0 | -
dal13.sr01.rk208 | DAL13 | 1 | 208 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108743 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 18 | 23 | 2 | 0 | 2 | 0 | 20 | 25 | 50 | 33 | 2 | 0 | 35 | 0 | 17 | 15 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 3380 | 3344 | 0 | 0 | 6.724 | 0.20376 | 7.1315 |  | -1.1315 | -5.5532 | - | 0 | -
dal13.sr01.rk209 | DAL13 | 1 | 209 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108745 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 15 | 20 | 3 | 0 | 3 | 2 | 20 | 25 | 50 | 27 | 4 | 2 | 33 | 0 | 23 | 17 | 21 | 23 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 2206 | 1858 | 0 | 0 | 4.064 | 0.15052 | 4.9671 |  | 1.0329 | 6.8622 | - | 0 | -
dal13.sr01.rk210 | DAL13 | 1 | 210 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108747 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 13 | 18 | 2 | 0 | 2 | 1 | 16 | 21 | 50 | 19 | 4 | 8 | 31 | 0 | 31 | 19 | 23 | 31 | 0 | 0.12 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2035 | 1942 | 0 | 0 | 3.977 | 0.20932 | 6.4888 |  | -0.48879 | -2.3352 | - | 0 | -
dal13.sr01.rk211 | DAL13 | 1 | 211 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108749 | 6 | 1 | L1 | Z6-375 | 19 |  |  | 16 | 21 | 2 | 0 | 2 | 0 | 18 | 23 | 50 | 25 | 4 | 0 | 29 | 0 | 25 | 21 | 25 | 25 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 1844 | 1742 | 0 | 0 | 3.586 | 0.14344 | 4.1598 |  | 1.8402 | 12.8293 | E | 0 | -
dal13.sr01.rk212 | DAL13 | 1 | 212 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108751 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 10 | 15 | 3 | 0 | 3 | 2 | 15 | 20 | 50 | 26 | 6 | 2 | 34 | 0 | 24 | 16 | 22 | 24 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 1451 | 1393 | 0 | 0 | 2.844 | 0.10938 | 3.7191 |  | 2.2809 | 20.8523 | S | 0 | -
dal13.sr01.rk213 | DAL13 | 1 | 213 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108753 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 14 | 19 | 6 | 0 | 6 | 0 | 20 | 25 | 50 | 22 | 8 | 0 | 30 | 0 | 28 | 20 | 28 | 28 | 0 | 0.12 | 2.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2073 | 1976 | 0 | 0 | 4.049 | 0.18405 | 5.5214 |  | 0.47864 | 2.6006 | - | 0 | -
dal13.sr01.rk214 | DAL13 | 1 | 214 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108755 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 13 | 18 | 6 | 0 | 6 | 1 | 20 | 25 | 50 | 24 | 10 | 8 | 42 | 0 | 26 | 8 | 18 | 26 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2183 | 1708 | 0 | 0 | 3.891 | 0.16212 | 6.8092 |  | -0.80925 | -4.9915 | - | 0 | -
dal13.sr01.rk215 | DAL13 | 1 | 215 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108757 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 20 | 25 | 2 | 0 | 2 | 3 | 24 | 30 | 50 | 29 | 3 | 10 | 42 | 0 | 21 | 8 | 11 | 21 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 2416 | 2456 | 0 | 0 | 4.872 | 0.168 | 7.056 |  | -1.056 | -6.2857 | - | 0 | -
dal13.sr01.rk216 | DAL13 | 1 | 216 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108759 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 17 | 22 | 5 | 0 | 5 | 1 | 23 | 28 | 50 | 30 | 5 | 1 | 36 | 0 | 20 | 14 | 19 | 20 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 2046 | 1968 | 0 | 0 | 4.014 | 0.1338 | 4.8168 |  | 1.1832 | 8.843 | - | 0 | -
dal13.sr01.rk217 | DAL13 | 1 | 217 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108761 | 5 | 1 | L1 | Z6-375 | 20 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk218 | DAL13 | 1 | 218 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108763 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 14 | 20 | 4 | 0 | 4 | 3 | 21 | 27 | 50 | 24 | 5 | 4 | 33 | 0 | 26 | 17 | 22 | 26 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2030 | 2196 | 0 | 0 | 4.226 | 0.17608 | 5.8108 |  | 0.18925 | 1.0748 | - | 0 | -
dal13.sr01.rk219 | DAL13 | 1 | 219 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108765 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 13 | 18 | 6 | 0 | 6 | 0 | 19 | 24 | 50 | 20 | 10 | 0 | 30 | 0 | 30 | 20 | 30 | 30 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 1655 | 1577 | 0 | 0 | 3.232 | 0.1616 | 4.848 |  | 1.152 | 7.1287 | - | 0 | -
dal13.sr01.rk220 | DAL13 | 1 | 220 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108767 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 17 | 22 | 2 | 0 | 2 | 1 | 19 | 25 | 50 | 27 | 4 | 1 | 32 | 0 | 23 | 18 | 22 | 23 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2374 | 2297 | 0 | 0 | 4.671 | 0.173 | 5.536 |  | 0.464 | 2.6821 | - | 0 | -
dal13.sr01.rk221 | DAL13 | 1 | 221 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108769 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 23 | 28 | 6 | 0 | 6 | 0 | 29 | 34 | 50 | 36 | 8 | 0 | 44 | 0 | 14 | 6 | 14 | 14 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2953 | 3041 | 0 | 0 | 5.994 | 0.1665 | 7.326 |  | -1.326 | -7.964 | - | 0 | -
dal13.sr01.rk222 | DAL13 | 1 | 222 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108771 | 6 | 1 | L1 | Z6-375 | 20 |  |  | 14 | 19 | 5 | 0 | 5 | 0 | 19 | 24 | 50 | 30 | 8 | 0 | 38 | 0 | 20 | 12 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 2669 | 2046 | 0 | 0 | 4.715 | 0.15717 | 5.9723 |  | 0.027667 | 0.17603 | E | 0 | -
dal13.sr01.rk223 | DAL13 | 1 | 223 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108773 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 17 | 22 | 0 | 0 | 0 | 0 | 17 | 22 | 50 | 25 | 0 | 0 | 25 | 0 | 25 | 25 | 25 | 25 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-102 | 2824 | 2540 | 0 | 0 | 5.364 | 0.21456 | 5.364 |  | 0.636 | 2.9642 | S | 0 | -
dal13.sr01.rk224 | DAL13 | 1 | 224 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108775 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 7 | 12 | 1 | 0 | 1 | 1 | 9 | 14 | 50 | 12 | 1 | 1 | 14 | 0 | 38 | 36 | 37 | 38 | 0 | 0.12 | 3.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 1237 | 873 | 0 | 0 | 2.11 | 0.17583 | 2.4617 |  | 3.5383 | 20.1232 | - | 0 | -
dal13.sr01.rk225 | DAL13 | 1 | 225 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108777 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 11 | 16 | 0 | 0 | 0 | 0 | 11 | 16 | 50 | 17 | 0 | 0 | 17 | 0 | 33 | 33 | 33 | 33 | 0 | 0.12 | 3 | 0 | Bare Metal - Live | N | DAL13-102 | 1528 | 1644 | 0 | 0 | 3.172 | 0.18659 | 3.172 |  | 2.828 | 15.1564 | - | 0 | -
dal13.sr01.rk226 | DAL13 | 1 | 226 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108779 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 13 | 18 | 1 | 0 | 1 | 0 | 14 | 19 | 50 | 18 | 1 | 0 | 19 | 0 | 32 | 31 | 32 | 32 | 0 | 0.12 | 2.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 1731 | 2277 | 0 | 0 | 4.008 | 0.22267 | 4.2307 |  | 1.7693 | 7.9461 | - | 0 | -
dal13.sr01.rk227 | DAL13 | 1 | 227 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108781 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 14 | 19 | 0 | 0 | 0 | 1 | 15 | 20 | 50 | 22 | 0 | 1 | 23 | 0 | 28 | 27 | 27 | 28 | 0 | 0.12 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 2868 | 2893 | 0 | 0 | 5.761 | 0.26186 | 6.0229 |  | -0.022864 | -0.087311 | - | 0 | -
dal13.sr01.rk228 | DAL13 | 1 | 228 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108783 | 5 | 1 | L1 | Z5-375 | 21 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk229 | DAL13 | 1 | 229 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108785 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 12 | 17 | 0 | 0 | 0 | 1 | 13 | 18 | 50 | 17 | 0 | 1 | 18 | 0 | 33 | 32 | 32 | 33 | 0 | 0.12 | 2.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 1682 | 2067 | 0 | 0 | 3.749 | 0.22053 | 3.9695 |  | 2.0305 | 9.2073 | - | 0 | -
dal13.sr01.rk230 | DAL13 | 1 | 230 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108787 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 31 | 36 | 0 | 0 | 0 | 2 | 33 | 38 | 50 | 36 | 0 | 2 | 38 | 0 | 14 | 12 | 12 | 14 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-102 | 4928 | 4485 | 0 | 0 | 9.413 | 0.26147 | 9.9359 |  | -3.9359 | -15.053 | - | 0 | -
dal13.sr01.rk231 | DAL13 | 1 | 231 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108789 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 27 | 32 | 2 | 0 | 2 | 1 | 30 | 35 | 50 | 36 | 3 | 1 | 40 | 0 | 14 | 10 | 13 | 14 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 4663 | 4552 | 0 | 0 | 9.215 | 0.25597 | 10.2389 |  | -4.2389 | -16.56 | - | 0 | -
dal13.sr01.rk232 | DAL13 | 1 | 232 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108791 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 17 | 22 | 2 | 0 | 2 | 0 | 19 | 24 | 50 | 36 | 3 | 0 | 39 | 0 | 14 | 11 | 14 | 14 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-102 | 2319 | 2344 | 0 | 0 | 4.663 | 0.12953 | 5.0516 |  | 0.94842 | 7.3221 | - | 0 | -
dal13.sr01.rk233 | DAL13 | 1 | 233 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108793 | 6 | 1 | L1 | Z5-375 | 21 |  |  | 17 | 22 | 3 | 0 | 3 | 1 | 21 | 26 | 50 | 29 | 3 | 1 | 33 | 0 | 21 | 17 | 20 | 21 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 2808 | 2191 | 0 | 0 | 4.999 | 0.17238 | 5.6885 |  | 0.31148 | 1.807 | E | 0 | -
dal13.sr01.rk234 | DAL13 | 1 | 234 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108795 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | S | 1 | -
dal13.sr01.rk235 | DAL13 | 1 | 235 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108797 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 2 | -
dal13.sr01.rk236 | DAL13 | 1 | 236 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108799 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.12 | 2.5455 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk237 | DAL13 | 1 | 237 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108801 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk238 | DAL13 | 1 | 238 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108803 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 16 | 0 | 0 | 16 | 0 | 34 | 34 | 34 | 34 | 0 | 0.12 | 3.0909 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk239 | DAL13 | 1 | 239 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108805 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.12 | 4.4545 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk240 | DAL13 | 1 | 240 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108807 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.12 | 4.4545 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk241 | DAL13 | 1 | 241 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108809 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 1 | -
dal13.sr01.rk242 | DAL13 | 1 | 242 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108811 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 2 | -
dal13.sr01.rk243 | DAL13 | 1 | 243 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108813 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 6 | 0 | 0 | 6 | 0 | 44 | 44 | 44 | 44 | 0 | 0.12 | 4 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk244 | DAL13 | 1 | 244 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1108815 | 6 | 1 | L1 | Z6-375 | 22 |  |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 14 | 0 | 0 | 14 | 0 | 36 | 36 | 36 | 36 | 0 | 0.12 | 3.2727 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | E | 0 | -
dal13.sr01.rk245 | DAL13 | 1 | 245 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108817 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 22 | 27 | 2 | 0 | 2 | 0 | 24 | 29 | 50 | 32 | 4 | 0 | 36 | 0 | 18 | 14 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2629 | 2631 | 0 | 0 | 5.26 | 0.16437 | 5.9175 |  | 0.0825 | 0.5019 | S | 0 | -
dal13.sr01.rk246 | DAL13 | 1 | 246 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108819 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 16 | 21 | 5 | 0 | 5 | 0 | 21 | 26 | 50 | 22 | 6 | 0 | 28 | 0 | 28 | 22 | 28 | 28 | 0 | 0.12 | 2.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 1866 | 2249 | 0 | 0 | 4.115 | 0.18705 | 5.2373 |  | 0.76273 | 4.0778 | - | 0 | -
dal13.sr01.rk247 | DAL13 | 1 | 247 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108821 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 14 | 19 | 4 | 0 | 4 | 0 | 18 | 23 | 50 | 24 | 7 | 0 | 31 | 0 | 26 | 19 | 26 | 26 | 0 | 0.12 | 2.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2331 | 2186 | 0 | 0 | 4.517 | 0.18821 | 5.8345 |  | 0.16554 | 0.87957 | - | 0 | -
dal13.sr01.rk248 | DAL13 | 1 | 248 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108823 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 24 | 29 | 3 | 0 | 3 | 2 | 29 | 34 | 50 | 33 | 5 | 2 | 40 | 0 | 17 | 10 | 15 | 17 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 4195 | 3705 | 0 | 0 | 7.9 | 0.23939 | 9.5758 |  | -3.5758 | -14.9367 | - | 0 | -
dal13.sr01.rk249 | DAL13 | 1 | 249 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108825 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 23 | 28 | 1 | 0 | 1 | 1 | 25 | 30 | 50 | 38 | 1 | 1 | 40 | 0 | 12 | 10 | 11 | 12 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 3354 | 3561 | 0 | 0 | 6.915 | 0.18197 | 7.2789 |  | -1.2789 | -7.0282 | - | 0 | -
dal13.sr01.rk250 | DAL13 | 1 | 250 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108827 | 5 | 1 | L1 | Z5-375 | 23 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk251 | DAL13 | 1 | 251 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108829 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 20 | 25 | 1 | 0 | 1 | 0 | 21 | 26 | 50 | 33 | 8 | 0 | 41 | 0 | 17 | 9 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 4514 | 4513 | 0 | 0 | 9.027 | 0.27355 | 11.2154 |  | -5.2154 | -19.0658 | - | 0 | -
dal13.sr01.rk252 | DAL13 | 1 | 252 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108831 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 17 | 22 | 7 | 0 | 7 | 1 | 25 | 30 | 50 | 29 | 9 | 1 | 39 | 0 | 21 | 11 | 20 | 21 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 2985 | 2972 | 0 | 0 | 5.957 | 0.20541 | 8.0111 |  | -2.0111 | -9.7907 | - | 0 | -
dal13.sr01.rk253 | DAL13 | 1 | 253 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108833 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 17 | 22 | 0 | 0 | 0 | 1 | 17 | 23 | 50 | 32 | 0 | 2 | 34 | 0 | 18 | 16 | 16 | 18 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2923 | 3200 | 0 | 0 | 6.123 | 0.19134 | 6.5057 |  | -0.50569 | -2.6428 | - | 0 | -
dal13.sr01.rk254 | DAL13 | 1 | 254 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108835 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 20 | 25 | 1 | 0 | 1 | 1 | 21 | 27 | 50 | 33 | 2 | 1 | 36 | 0 | 17 | 14 | 16 | 17 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 3439 | 3366 | 0 | 0 | 6.805 | 0.20621 | 7.4236 |  | -1.4236 | -6.9037 | - | 0 | -
dal13.sr01.rk255 | DAL13 | 1 | 255 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108837 | 6 | 1 | L1 | Z5-375 | 23 |  |  | 18 | 23 | 5 | 0 | 5 | 0 | 23 | 28 | 50 | 26 | 16 | 0 | 42 | 0 | 24 | 8 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2525 | 2521 | 0 | 0 | 5.046 | 0.19408 | 8.1512 |  | -2.1512 | -11.0844 | E | 0 | -
dal13.sr01.rk256 | DAL13 | 1 | 256 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108839 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 14 | 19 | 4 | 0 | 4 | 0 | 16 | 23 | 50 | 22 | 14 | 0 | 36 | 0 | 28 | 14 | 28 | 28 | 0 | 0.12 | 2.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 2335 | 2436 | 0 | 0 | 4.771 | 0.21686 | 7.8071 |  | -1.8071 | -8.3328 | S | 0 | -
dal13.sr01.rk257 | DAL13 | 1 | 257 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108841 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 7 | 12 | 2 | 0 | 2 | 1 | 10 | 15 | 50 | 15 | 3 | 1 | 19 | 0 | 35 | 31 | 34 | 35 | 0 | 0.12 | 3.0909 | 0 | Bare Metal - Live | N | DAL13-102 | 1121 | 917 | 0 | 0 | 2.038 | 0.13587 | 2.5815 |  | 3.4185 | 25.1609 | - | 0 | -
dal13.sr01.rk258 | DAL13 | 1 | 258 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108843 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 9 | 14 | 6 | 0 | 6 | 0 | 15 | 20 | 50 | 16 | 12 | 0 | 28 | 0 | 34 | 22 | 34 | 34 | 0 | 0.12 | 3.0909 | 0 | Bare Metal - Live | N | DAL13-102 | 2031 | 1986 | 0 | 0 | 4.017 | 0.25106 | 7.0298 |  | -1.0298 | -4.1016 | - | 0 | -
dal13.sr01.rk259 | DAL13 | 1 | 259 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108845 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 14 | 19 | 0 | 0 | 0 | 0 | 14 | 19 | 50 | 20 | 0 | 0 | 20 | 0 | 30 | 30 | 30 | 30 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 1999 | 2002 | 0 | 0 | 4.001 | 0.20005 | 4.001 |  | 1.999 | 9.9925 | - | 0 | -
dal13.sr01.rk260 | DAL13 | 1 | 260 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108847 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 12 | 17 | 1 | 0 | 1 | 0 | 13 | 18 | 50 | 23 | 2 | 0 | 25 | 0 | 27 | 25 | 27 | 27 | 0 | 0.12 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 2170 | 2071 | 0 | 0 | 4.241 | 0.18439 | 4.6098 |  | 1.3902 | 7.5395 | - | 0 | -
dal13.sr01.rk261 | DAL13 | 1 | 261 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1108849 | 5 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk262 | DAL13 | 1 | 262 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108851 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 13 | 18 | 2 | 0 | 2 | 0 | 15 | 20 | 50 | 29 | 2 | 0 | 31 | 0 | 21 | 19 | 21 | 21 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 1622 | 2032 | 0 | 0 | 3.654 | 0.126 | 3.906 |  | 2.094 | 16.619 | - | 0 | -
dal13.sr01.rk263 | DAL13 | 1 | 263 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108853 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 15 | 20 | 2 | 0 | 2 | 0 | 17 | 22 | 50 | 27 | 2 | 0 | 29 | 0 | 23 | 21 | 23 | 23 | 0 | 0.12 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-102 | 1716 | 1792 | 0 | 0 | 3.508 | 0.12993 | 3.7679 |  | 2.2321 | 17.1802 | - | 0 | -
dal13.sr01.rk264 | DAL13 | 1 | 264 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108855 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 19 | 24 | 1 | 0 | 1 | 0 | 20 | 25 | 50 | 26 | 2 | 0 | 28 | 0 | 24 | 22 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3577 | 3503 | 0 | 0 | 7.08 | 0.27231 | 7.6246 |  | -1.6246 | -5.9661 | - | 0 | -
dal13.sr01.rk265 | DAL13 | 1 | 265 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108857 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 7 | 12 | 5 | 0 | 5 | 0 | 12 | 17 | 50 | 18 | 9 | 0 | 27 | 0 | 32 | 23 | 32 | 32 | 0 | 0.12 | 2.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 1387 | 1317 | 0 | 0 | 2.704 | 0.15022 | 4.056 |  | 1.944 | 12.9408 | - | 0 | -
dal13.sr01.rk266 | DAL13 | 1 | 266 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1108859 | 6 | 1 | L1 | Z5-375 | 24 | vlam - 10/10/2022 - Informed by SM that this is now POD2. |  | 40 | 45 | 0 | 0 | 0 | 0 | 40 | 45 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.12 | 0.45455 | 0 | Bare Metal - Live | N | DAL13-102 | 2146 | 2116 | 0 | 0 | 4.262 | 0.094711 | 4.262 |  | 1.738 | 18.3505 | E | 0 | -
dal13.sr01.rk267 | DAL13 | 1 | 267 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1108861 | 20 | 1 | L1 | Z5-375 | 25 | vlam - vlam - 10/12/21 - NGDC Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | S | 0 | -
dal13.sr01.rk268 | DAL13 | 1 | 268 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1108863 | 20 | 1 | L1 | Z5-375 | 25 | vlam - vlam - 10/12/21 - NGDC Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr01.rk269 | DAL13 | 1 | 269 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1108865 | 20 | 1 | L1 | Z5-375 | 25 | vlam - vlam - 10/12/21 - NGDC Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr01.rk270 | DAL13 | 1 | 270 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1108867 | 20 | 1 | L1 | Z5-375 | 25 | vlam - vlam - 10/12/21 - NGDC Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr01.rk271 | DAL13 | 1 | 271 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108869 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.2 | 4.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 10 | 0 | - | 0 | -
dal13.sr01.rk272 | DAL13 | 1 | 272 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108871 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 50 | 1 | 0 | 1 | 2 | 0 | 49 | 48 | 48 | 49 | 0 | 0.2 | 4.3636 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk273 | DAL13 | 1 | 273 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108873 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.2 | 4.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk274 | DAL13 | 1 | 274 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108875 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk275 | DAL13 | 1 | 275 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108877 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 2 | 50 | 1 | 1 | 0 | 2 | 0 | 49 | 48 | 49 | 49 | 0 | 0.2 | 4.4545 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk276 | DAL13 | 1 | 276 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108879 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 2 | 50 | 1 | 1 | 0 | 2 | 0 | 49 | 48 | 49 | 49 | 0 | 0.2 | 4.4545 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk277 | DAL13 | 1 | 277 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108881 | 10 | 1 | L1 | Z5-375 | 25 |  |  | 24 | 25 | 0 | 0 | 0 | 1 | 24 | 26 | 50 | 26 | 0 | 1 | 27 | 0 | 24 | 23 | 23 | 24 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk278 | DAL13 | 1 | 278 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108883 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk279 | DAL13 | 1 | 279 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108885 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 22 | 24 | 0 | 0 | 0 | 1 | 22 | 25 | 50 | 25 | 0 | 1 | 26 | 0 | 25 | 24 | 24 | 25 | 0 | 0.2 | 2.1818 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk280 | DAL13 | 1 | 280 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108887 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 24 | 27 | 0 | 0 | 0 | 0 | 24 | 27 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.2 | 2 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk281 | DAL13 | 1 | 281 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108889 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 24 | 24 | 3 | 0 | 3 | 0 | 24 | 27 | 50 | 25 | 3 | 0 | 28 | 0 | 25 | 22 | 25 | 25 | 0 | 0.2 | 2.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk282 | DAL13 | 1 | 282 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108891 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk283 | DAL13 | 1 | 283 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108893 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 24 | 27 | 0 | 0 | 0 | 0 | 24 | 27 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.2 | 2 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk284 | DAL13 | 1 | 284 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108895 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 24 | 27 | 0 | 0 | 0 | 0 | 24 | 27 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.2 | 2 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk285 | DAL13 | 1 | 285 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108897 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.2 | 4.4545 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk286 | DAL13 | 1 | 286 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108899 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk287 | DAL13 | 1 | 287 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108901 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk288 | DAL13 | 1 | 288 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108903 | 10 | 1 | L1 | Z5-375 | 26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk289 | DAL13 | 1 | 289 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108905 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 50 | 0 | 0 | 1 | 1 | 0 | 50 | 49 | 49 | 50 | 0 | 0.2 | 4.4545 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk290 | DAL13 | 1 | 290 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108907 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 49 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk291 | DAL13 | 1 | 291 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108909 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk292 | DAL13 | 1 | 292 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108911 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 1 | 0 | 1 | 0 | 24 | 27 | 50 | 27 | 1 | 0 | 28 | 0 | 23 | 22 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk293 | DAL13 | 1 | 293 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108913 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk294 | DAL13 | 1 | 294 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108915 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 25 | 0 | 0 | 0 | 1 | 24 | 26 | 50 | 26 | 0 | 1 | 27 | 0 | 24 | 23 | 23 | 24 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk295 | DAL13 | 1 | 295 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108917 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk296 | DAL13 | 1 | 296 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108919 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk297 | DAL13 | 1 | 297 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108921 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk298 | DAL13 | 1 | 298 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108923 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 26 | 0 | 0 | 0 | 0 | 24 | 26 | 50 | 27 | 0 | 0 | 27 | 0 | 23 | 23 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk299 | DAL13 | 1 | 299 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108925 | 10 | 1 | L1 | Z6-375 | 27 |  |  | 24 | 25 | 0 | 0 | 0 | 1 | 24 | 26 | 50 | 26 | 0 | 1 | 27 | 0 | 24 | 23 | 23 | 24 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 10 | 0 | E | 0 | -
dal13.sr01.rk300 | DAL13 | 1 | 300 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108927 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 25 | 1 | 0 | 1 | 0 | 24 | 26 | 50 | 26 | 1 | 0 | 27 | 0 | 24 | 23 | 24 | 24 | 0 | 0.2 | 2.1818 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk301 | DAL13 | 1 | 301 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108929 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 25 | 0 | 0 | 0 | 1 | 24 | 26 | 50 | 26 | 0 | 1 | 27 | 0 | 24 | 23 | 23 | 24 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk302 | DAL13 | 1 | 302 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108931 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 26 | 1 | 0 | 1 | 0 | 24 | 27 | 50 | 27 | 1 | 0 | 28 | 0 | 23 | 22 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk303 | DAL13 | 1 | 303 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108933 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 26 | 1 | 0 | 1 | 0 | 24 | 27 | 50 | 27 | 1 | 0 | 28 | 0 | 23 | 22 | 23 | 23 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk304 | DAL13 | 1 | 304 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108935 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 26 | 0 | 0 | 0 | 1 | 24 | 27 | 50 | 27 | 0 | 1 | 28 | 0 | 23 | 22 | 22 | 23 | 0 | 0.2 | 2 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk305 | DAL13 | 1 | 305 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108937 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 25 | 0 | 0 | 0 | 1 | 24 | 26 | 50 | 26 | 0 | 1 | 27 | 0 | 24 | 23 | 23 | 24 | 0 | 0.2 | 2.0909 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk306 | DAL13 | 1 | 306 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108939 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 24 | 26 | 0 | 0 | 0 | 1 | 24 | 27 | 50 | 27 | 0 | 1 | 28 | 0 | 23 | 22 | 22 | 23 | 0 | 0.2 | 2 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk307 | DAL13 | 1 | 307 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108941 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk308 | DAL13 | 1 | 308 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108943 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk309 | DAL13 | 1 | 309 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108945 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.2 | 4.5455 | 0 | Gen1 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk310 | DAL13 | 1 | 310 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1108947 | 10 | 1 | L1 | Z6-375 | 28 |  |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 10 | 0 | 0 | 10 | 0 | 40 | 40 | 40 | 40 | 0 | 0.2 | 3.6364 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk311 | DAL13 | 1 | 311 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 3510895 | 15 | 2 | L2 | Z1-375 | 29 | ysilva - ysilva - 9/14/2023 - Allocated to Gen2-Network per DCL-3090 |  | 21 | 28 | 0 | 0 | 0 | 0 | 21 | 28 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.3 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | S | 0 | -
dal13.sr01.rk312 | DAL13 | 1 | 312 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 3510897 | 15 | 2 | L2 | Z1-375 | 29 | ysilva - ysilva - 9/14/2023 - Allocated to Gen2-Network per DCL-3090 |  | 21 | 28 | 0 | 0 | 0 | 0 | 21 | 28 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.3 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk313 | DAL13 | 1 | 313 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3508621 | 15 | 2 | L2 | Z1-375 | 29 | ysilva - ysilva - 9/14/2023 - Allocated to Gen2-Compute per DCL-3090. |  | 21 | 24 | 0 | 0 | 0 | 0 | 21 | 24 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.3 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk314 | DAL13 | 1 | 314 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3508623 | 15 | 2 | L2 | Z1-375 | 29 | ysilva - ysilva - 9/14/2023 - Allocated to Gen2-Compute per DCL-3090. |  | 21 | 24 | 0 | 0 | 0 | 0 | 21 | 24 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.3 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk315 | DAL13 | 1 | 315 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3508925 | 15 | 2 | L2 | Z1-375 | 29 | ysilva - ysilva - 9/14/2023 - Allocated to Gen2-Compute per DCL-3090. |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.3 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk316 | DAL13 | 1 | 316 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441319 | 10 | 2 | L2 | Z1-375 | 29 |  |  | 27 | 33 | 0 | 0 | 0 | 0 | 27 | 33 | 50 | 57 | 0 | 0 | 57 | 0 | -7 | -7 | -7 | -7 | 0 | 0.2 | -0.63636 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk317 | DAL13 | 1 | 317 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441321 | 10 | 2 | L2 | Z1-375 | 29 |  |  | 27 | 33 | 0 | 0 | 0 | 0 | 27 | 33 | 50 | 57 | 0 | 0 | 57 | 0 | -7 | -7 | -7 | -7 | 0 | 0.2 | -0.63636 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk318 | DAL13 | 1 | 318 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441323 | 10 | 2 | L2 | Z1-375 | 29 |  |  | 23 | 23 | 6 | 0 | 6 | 4 | 27 | 33 | 50 | 29 | 24 | 4 | 57 | 0 | 21 | -7 | 17 | 21 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk319 | DAL13 | 1 | 319 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441325 | 10 | 2 | L2 | Z1-375 | 29 |  |  | 26 | 26 | 6 | 0 | 6 | 1 | 27 | 33 | 50 | 32 | 24 | 1 | 57 | 0 | 18 | -7 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk320 | DAL13 | 1 | 320 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441327 | 10 | 2 | L2 | Z1-375 | 29 |  |  | 27 | 27 | 6 | 0 | 6 | 0 | 27 | 33 | 50 | 33 | 24 | 0 | 57 | 0 | 17 | -7 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk321 | DAL13 | 1 | 321 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441329 | 10 | 2 | L2 | Z1-375 | 29 |  |  | 27 | 27 | 6 | 0 | 6 | 0 | 27 | 33 | 50 | 33 | 24 | 0 | 57 | 0 | 17 | -7 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk322 | DAL13 | 1 | 322 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 57 | 1708167 | 10 | 2 | L2 | Z1-375 | 30 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 57 | 36 | 24 | 0 | 60 | 0 | 21 | -3 | 21 | 21 | 0 | 0.17544 | 1.9091 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk323 | DAL13 | 1 | 323 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 57 | 1708169 | 10 | 2 | L2 | Z1-375 | 30 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 57 | 36 | 24 | 0 | 60 | 0 | 21 | -3 | 21 | 21 | 0 | 0.17544 | 1.9091 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk324 | DAL13 | 1 | 324 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 57 | 1708171 | 10 | 2 | L2 | Z1-375 | 30 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 57 | 36 | 24 | 0 | 60 | 0 | 21 | -3 | 21 | 21 | 0 | 0.17544 | 1.9091 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk325 | DAL13 | 1 | 325 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 57 | 1708173 | 10 | 2 | L2 | Z1-375 | 30 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 26 | 29 | 7 | 0 | 7 | 0 | 27 | 36 | 57 | 35 | 25 | 0 | 60 | 0 | 22 | -3 | 22 | 22 | 0 | 0.17544 | 2 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk326 | DAL13 | 1 | 326 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3137734 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 21 | 24 | 0 | 0 | 0 | 1 | 22 | 25 | 50 | 47 | 0 | 2 | 49 | 0 | 3 | 1 | 1 | 3 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk327 | DAL13 | 1 | 327 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3137736 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk328 | DAL13 | 1 | 328 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3137738 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 21 | 24 | 1 | 0 | 1 | 0 | 22 | 25 | 50 | 47 | 2 | 0 | 49 | 0 | 3 | 1 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk329 | DAL13 | 1 | 329 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3137740 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.4 | 0.18182 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk330 | DAL13 | 1 | 330 | G1 | 10G | Dual Path | Sellable | Gen2 | Bare Metal | Live | 50 | 3137742 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 9 | 12 | 0 | 0 | 0 | 0 | 9 | 12 | 50 | 19 | 0 | 0 | 19 | 0 | 31 | 31 | 31 | 31 | 0 | 0.4 | 2.8182 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk331 | DAL13 | 1 | 331 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 1908302 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.4 | 0.18182 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk332 | DAL13 | 1 | 332 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 1908304 | 20 | 2 | L2 | Z1-375 | 30 |  |  | 23 | 26 | 0 | 0 | 0 | 0 | 23 | 26 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.4 | 0.45455 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | E | 0 | -
dal13.sr01.rk333 | DAL13 | 1 | 333 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441493 | 10 | 2 | L2 | Z1-375 | 31 |  |  | 25 | 25 | 6 | 0 | 6 | 2 | 27 | 33 | 50 | 31 | 24 | 2 | 57 | 0 | 19 | -7 | 17 | 19 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk334 | DAL13 | 1 | 334 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441495 | 10 | 2 | L2 | Z1-375 | 31 |  |  | 25 | 25 | 6 | 0 | 6 | 2 | 27 | 33 | 50 | 31 | 24 | 2 | 57 | 0 | 19 | -7 | 17 | 19 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk335 | DAL13 | 1 | 335 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441497 | 10 | 2 | L2 | Z1-375 | 31 |  |  | 27 | 27 | 6 | 0 | 6 | 0 | 27 | 33 | 50 | 33 | 24 | 0 | 57 | 0 | 17 | -7 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk336 | DAL13 | 1 | 336 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441499 | 10 | 2 | L2 | Z1-375 | 31 |  |  | 27 | 27 | 6 | 0 | 6 | 0 | 27 | 33 | 50 | 33 | 24 | 0 | 57 | 0 | 17 | -7 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk337 | DAL13 | 1 | 337 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441501 | 10 | 2 | L2 | Z1-375 | 31 |  |  | 27 | 27 | 6 | 0 | 6 | 0 | 27 | 33 | 50 | 33 | 24 | 0 | 57 | 0 | 17 | -7 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk338 | DAL13 | 1 | 338 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3539382 | 20 | 2 | L2 | Z1-375 | 31 | ysilva - vlam - 2/9/2024 - Allocated to NG for Flex per DCL-3090. |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk339 | DAL13 | 1 | 339 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3539384 | 20 | 2 | L2 | Z1-375 | 31 | ysilva - vlam - 2/9/2024 - Allocated to NG for Flex per DCL-3090. |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk340 | DAL13 | 1 | 340 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3539386 | 20 | 2 | L2 | Z1-375 | 31 | ysilva - vlam - 2/9/2024 - Allocated to NG for Flex per DCL-3090. |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk341 | DAL13 | 1 | 341 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Live | 50 | 3536266 | 20 | 2 | L2 | Z1-375 | 31 | ysilva - 2/22/2024 - Allocated to NG2-GPU per DCL-3090 |  | 11 | 15 | 0 | 0 | 0 | 0 | 11 | 15 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.4 | 2 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk342 | DAL13 | 1 | 342 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Live | 50 | 3536268 | 20 | 2 | L2 | Z1-375 | 31 | ysilva - 2/22/2024 - Allocated to NG2-GPU per DCL-3090 |  | 11 | 15 | 0 | 0 | 0 | 0 | 11 | 15 | 50 | 28 | 0 | 0 | 28 | 0 | 22 | 22 | 22 | 22 | 0 | 0.4 | 2 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk343 | DAL13 | 1 | 343 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441513 | 10 | 2 | L2 | Z1-375 | 31 |  |  | 26 | 26 | 6 | 0 | 6 | 1 | 27 | 33 | 50 | 32 | 24 | 1 | 57 | 0 | 18 | -7 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk344 | DAL13 | 1 | 344 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3041658 | 20 | 2 | L2 | Z2-375 | 32 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr01.rk345 | DAL13 | 1 | 345 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3041660 | 20 | 2 | L2 | Z2-375 | 32 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk346 | DAL13 | 1 | 346 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3041662 | 20 | 2 | L2 | Z2-375 | 32 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk347 | DAL13 | 1 | 347 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3041664 | 20 | 2 | L2 | Z2-375 | 32 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk348 | DAL13 | 1 | 348 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3041666 | 20 | 2 | L2 | Z2-375 | 32 |  |  | 18 | 21 | 0 | 0 | 0 | 0 | 18 | 21 | 50 | 35 | 0 | 0 | 35 | 0 | 15 | 15 | 15 | 15 | 0 | 0.4 | 1.3636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk349 | DAL13 | 1 | 349 | G1 | 10G | Dual Path | Sellable | Gen2 | Zseries | Live | 50 | 3041668 | 10 | 2 | L2 | Z2-375 | 32 |  |  | 0 | 6 | 2 | 0 | 2 | 0 | 0 | 8 | 50 | 6 | 3 | 0 | 9 | 0 | 44 | 41 | 44 | 44 | 0 | 0.2 | 4 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk350 | DAL13 | 1 | 350 | G1 | 10G | Dual Path | Sellable | Gen2 | Zseries | Live | 0 | 3058360 | 10 | 2 | L2 | Z2-375 | 32 | vlam - vlam - 11/03/20 - DAL13.SR01.RK350-352 – Allocated for Z-series. Rk350 already built. |  | 13 | 19 | 2 | 0 | 2 | 0 | 15 | 21 | 50 | 37 | 2 | 0 | 39 | 0 | 13 | 11 | 13 | 13 | 0 | 0.2 | 1.1818 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk351 | DAL13 | 1 | 351 | G1 | 10G | Dual Path | Sellable | Gen2 | Zseries | Live | 50 | 3466134 | 10 | 2 | L2 | Z2-375 | 32 | vlam - 4/18/2022 - Allocated to NG Zseries per IMS ticket 145076032 |  | 11 | 16 | 2 | 0 | 2 | 0 | 12 | 18 | 50 | 31 | 5 | 0 | 36 | 0 | 19 | 14 | 19 | 19 | 0 | 0.2 | 1.7273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk352 | DAL13 | 1 | 352 | G1 | 10G | Dual Path | Sellable | Gen2 | Zseries | Live | 50 | 3466136 | 10 | 2 | L2 | Z2-375 | 32 | vlam - 4/18/2022 - Allocated to NG Zseries per IMS ticket 145076032 |  | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 9 | 0 | 0 | 9 | 0 | 41 | 41 | 41 | 41 | 0 | 0.2 | 3.7273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 10 | 0 | - | 0 | -
dal13.sr01.rk353 | DAL13 | 1 | 353 | G1 | 10G | Dual Path | Sellable | Gen2 | Zseries | Live | 50 | 3137968 | 10 | 2 | L2 | Z2-375 | 32 |  |  | 9 | 14 | 1 | 0 | 1 | 0 | 10 | 15 | 50 | 29 | 1 | 0 | 30 | 0 | 21 | 20 | 21 | 21 | 0 | 0.2 | 1.9091 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk354 | DAL13 | 1 | 354 | G1 | 10G | Dual Path | Sellable | Gen2 | Zseries | Live | 50 | 3116574 | 10 | 2 | L2 | Z2-375 | 32 |  |  | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 8 | 50 | 4 | 0 | 5 | 9 | 0 | 46 | 41 | 41 | 46 | 0 | 0.2 | 3.7273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk355 | DAL13 | 1 | 355 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 3112280 | 10 | 2 | L2 | Z2-375 | 33 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 50 | 36 | 24 | 0 | 60 | 0 | 14 | -10 | 14 | 14 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk356 | DAL13 | 1 | 356 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441595 | 10 | 2 | L2 | Z2-375 | 33 | mgill - This rack being retired was brought to my attention by Andy Coleman. Not sure how or why as was have no request to retire this rack and i can find nothing via slack either for the time this rack status was changed. Unsure if this was changed due to the DCIM export/import process either. Rack has been set to active status as requested by Andy. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 50 | 36 | 24 | 0 | 60 | 0 | 14 | -10 | 14 | 14 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk357 | DAL13 | 1 | 357 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441597 | 10 | 2 | L2 | Z2-375 | 33 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 50 | 36 | 24 | 0 | 60 | 0 | 14 | -10 | 14 | 14 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk358 | DAL13 | 1 | 358 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441599 | 10 | 2 | L2 | Z2-375 | 33 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 27 | 30 | 6 | 0 | 6 | 0 | 27 | 36 | 50 | 36 | 24 | 0 | 60 | 0 | 14 | -10 | 14 | 14 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk359 | DAL13 | 1 | 359 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441601 | 10 | 2 | L2 | Z2-375 | 33 |  |  | 22 | 22 | 9 | 0 | 9 | 5 | 27 | 36 | 50 | 28 | 27 | 5 | 60 | 0 | 22 | -10 | 17 | 22 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk360 | DAL13 | 1 | 360 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441603 | 10 | 2 | L2 | Z2-375 | 33 |  |  | 21 | 21 | 9 | 0 | 9 | 6 | 27 | 36 | 50 | 27 | 27 | 6 | 60 | 0 | 23 | -10 | 17 | 23 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk361 | DAL13 | 1 | 361 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441605 | 10 | 2 | L2 | Z2-375 | 33 |  |  | 24 | 24 | 9 | 0 | 9 | 3 | 27 | 36 | 50 | 30 | 27 | 3 | 60 | 0 | 20 | -10 | 17 | 20 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk362 | DAL13 | 1 | 362 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441607 | 10 | 2 | L2 | Z2-375 | 33 |  |  | 27 | 27 | 9 | 0 | 9 | 0 | 27 | 36 | 50 | 33 | 27 | 0 | 60 | 0 | 17 | -10 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk363 | DAL13 | 1 | 363 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441609 | 10 | 2 | L2 | Z2-375 | 33 | vlam - 3/25/2024 - Allocated to NG for NG2 - BAU per DCL-3669 |  | 25 | 25 | 9 | 0 | 9 | 2 | 27 | 36 | 50 | 31 | 27 | 2 | 60 | 0 | 19 | -10 | 17 | 19 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk364 | DAL13 | 1 | 364 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441611 | 10 | 2 | L2 | Z2-375 | 33 | vlam - 3/25/2024 - Allocated to NG for NG3 - BAU (SPR) per DCL-3669 |  | 26 | 26 | 9 | 0 | 9 | 1 | 27 | 36 | 50 | 32 | 27 | 1 | 60 | 0 | 18 | -10 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk365 | DAL13 | 1 | 365 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441613 | 10 | 2 | L2 | Z2-375 | 33 |  |  | 26 | 26 | 9 | 0 | 9 | 1 | 27 | 36 | 50 | 32 | 27 | 1 | 60 | 0 | 18 | -10 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk366 | DAL13 | 1 | 366 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3184076 | 20 | 2 | L2 | Z2-375 | 34 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr01.rk367 | DAL13 | 1 | 367 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3184078 | 20 | 2 | L2 | Z2-375 | 34 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk368 | DAL13 | 1 | 368 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3184080 | 20 | 2 | L2 | Z2-375 | 34 |  |  | 21 | 24 | 1 | 0 | 1 | 0 | 22 | 25 | 50 | 47 | 2 | 0 | 49 | 0 | 3 | 1 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk369 | DAL13 | 1 | 369 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3184082 | 20 | 2 | L2 | Z2-375 | 34 | vlam - vlam - 1/12/22 - This has been assigned to Gen2 per CAPREQ-667. |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk370 | DAL13 | 1 | 370 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3184084 | 20 | 2 | L2 | Z2-375 | 34 | vlam - vlam - 1/12/22 - This has been assigned to Gen2 per CAPREQ-667. |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk371 | DAL13 | 1 | 371 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 3184086 | 0 | 2 | L2 | Z2-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr01.rk372 | DAL13 | 1 | 372 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 3184088 | 0 | 2 | L2 | Z2-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr01.rk373 | DAL13 | 1 | 373 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 3184090 | 0 | 2 | L2 | Z2-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr01.rk374 | DAL13 | 1 | 374 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 3184092 | 0 | 2 | L2 | Z2-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr01.rk375 | DAL13 | 1 | 375 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 3184094 | 0 | 2 | L2 | Z2-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr01.rk376 | DAL13 | 1 | 376 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 3184096 | 0 | 2 | L2 | Z2-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 6 | -
dal13.sr01.rk377 | DAL13 | 1 | 377 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441331 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 25 | 28 | 6 | 0 | 6 | 2 | 27 | 36 | 50 | 34 | 24 | 2 | 60 | 0 | 16 | -10 | 14 | 16 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | S | 0 | -
dal13.sr01.rk378 | DAL13 | 1 | 378 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441333 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 26 | 29 | 6 | 0 | 6 | 1 | 27 | 36 | 50 | 35 | 24 | 1 | 60 | 0 | 15 | -10 | 14 | 15 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk379 | DAL13 | 1 | 379 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441335 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 25 | 28 | 6 | 0 | 6 | 2 | 27 | 36 | 50 | 34 | 24 | 2 | 60 | 0 | 16 | -10 | 14 | 16 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk380 | DAL13 | 1 | 380 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441337 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 26 | 29 | 6 | 0 | 6 | 1 | 27 | 36 | 50 | 35 | 24 | 1 | 60 | 0 | 15 | -10 | 14 | 15 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk381 | DAL13 | 1 | 381 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441339 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 25 | 28 | 6 | 0 | 6 | 2 | 27 | 36 | 50 | 34 | 24 | 2 | 60 | 0 | 16 | -10 | 14 | 16 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk382 | DAL13 | 1 | 382 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441341 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/8/2024 - This NG1 rack is for Staging or Development and will not be decommissioned. |  | 26 | 29 | 6 | 0 | 6 | 1 | 27 | 36 | 50 | 35 | 24 | 1 | 60 | 0 | 15 | -10 | 14 | 15 | 0 | 0.2 | 1.2727 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk383 | DAL13 | 1 | 383 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441343 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/5/2024 - Allocated to NG for NG2-BAU per DCL-3669 |  | 26 | 26 | 9 | 0 | 9 | 1 | 27 | 36 | 50 | 32 | 27 | 1 | 60 | 0 | 18 | -10 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk384 | DAL13 | 1 | 384 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441345 | 10 | 2 | L2 | Z3-375 | 35 | vlam - 4/5/2024 - Allocated to NG for NG2-BAU per DCL-3669 |  | 26 | 26 | 9 | 0 | 9 | 1 | 27 | 36 | 50 | 32 | 27 | 1 | 60 | 0 | 18 | -10 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk385 | DAL13 | 1 | 385 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441347 | 10 | 2 | L2 | Z3-375 | 35 |  |  | 26 | 26 | 9 | 0 | 9 | 1 | 27 | 36 | 50 | 32 | 27 | 1 | 60 | 0 | 18 | -10 | 17 | 18 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk386 | DAL13 | 1 | 386 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441349 | 10 | 2 | L2 | Z3-375 | 35 |  |  | 27 | 27 | 9 | 0 | 9 | 0 | 27 | 36 | 50 | 33 | 27 | 0 | 60 | 0 | 17 | -10 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | - | 0 | -
dal13.sr01.rk387 | DAL13 | 1 | 387 | G1 | 10G | Dual Path | Sellable | Gen1 | Compute | Live | 50 | 1441351 | 10 | 2 | L2 | Z3-375 | 35 |  |  | 27 | 27 | 9 | 0 | 9 | 0 | 27 | 36 | 50 | 33 | 27 | 0 | 60 | 0 | 17 | -10 | 17 | 17 | 0 | 0.2 | 1.5455 | 0 | Gen1 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 10 | 0 | E | 0 | -
dal13.sr01.rk388 | DAL13 | 1 | 388 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3221516 | 20 | 2 | L2 | Z3-375 | 36 | llarin - SL tag change per ticket:157582306 |  | 43 | 47 | 0 | 0 | 0 | 0 | 43 | 47 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr01.rk399 | DAL13 | 1 | 399 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441515 | 15 | 2 | L2 | Z1-375 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | S | 0 | -
dal13.sr01.rk400 | DAL13 | 1 | 400 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441517 | 15 | 2 | L2 | Z1-375 | 37 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 2 | 0 | 0 | 2 | 0 | 48 | 48 | 48 | 48 | 0 | 0.3 | 4.3636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk401 | DAL13 | 1 | 401 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441519 | 15 | 2 | L2 | Z1-375 | 37 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 2 | 0 | 0 | 2 | 0 | 48 | 48 | 48 | 48 | 0 | 0.3 | 4.3636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk402 | DAL13 | 1 | 402 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441521 | 15 | 2 | L2 | Z1-375 | 37 |  |  | 2 | 5 | 0 | 0 | 0 | 0 | 2 | 5 | 50 | 7 | 0 | 0 | 7 | 0 | 43 | 43 | 43 | 43 | 0 | 0.3 | 3.9091 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk403 | DAL13 | 1 | 403 | G1 | 10G | Dual Path | Unsellable | Gen2 | Management | Live | 50 | 1441523 | 15 | 2 | L2 | Z1-375 | 37 |  |  | 33 | 45 | 1 | 0 | 1 | 0 | 33 | 46 | 50 | 45 | 2 | 0 | 47 | 0 | 5 | 3 | 5 | 5 | 0 | 0.3 | 0.45455 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk404 | DAL13 | 1 | 404 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441525 | 15 | 2 | L2 | Z1-375 | 37 |  |  | 0 | 3 | 4 | 0 | 4 | 0 | 0 | 7 | 50 | 5 | 4 | 0 | 9 | 0 | 45 | 41 | 45 | 45 | 0 | 0.3 | 4.0909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk405 | DAL13 | 1 | 405 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441527 | 15 | 2 | L2 | Z2-375 | 37 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.3 | 4.4545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk406 | DAL13 | 1 | 406 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441529 | 15 | 2 | L2 | Z2-375 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk407 | DAL13 | 1 | 407 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441531 | 15 | 2 | L2 | Z2-375 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk408 | DAL13 | 1 | 408 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441533 | 15 | 2 | L2 | Z2-375 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk409 | DAL13 | 1 | 409 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441535 | 15 | 2 | L2 | Z2-375 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk410 | DAL13 | 1 | 410 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441537 | 15 | 2 | L2 | Z2-375 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | E | 0 | -
dal13.sr01.rk411 | DAL13 | 1 | 411 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3183926 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.4 | 0.45455 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr01.rk412 | DAL13 | 1 | 412 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3183928 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.4 | 0.45455 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr01.rk413 | DAL13 | 1 | 413 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3183930 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 19 | 22 | 0 | 0 | 0 | 0 | 19 | 22 | 50 | 43 | 0 | 0 | 43 | 0 | 7 | 7 | 7 | 7 | 0 | 0.4 | 0.63636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk414 | DAL13 | 1 | 414 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3183932 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.4 | 0.45455 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk415 | DAL13 | 1 | 415 | G1 | 10G | Dual Path | Sellable | Gen2 | Bare Metal | Live | 50 | 3183934 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 43 | 47 | 0 | 0 | 0 | 0 | 43 | 47 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk416 | DAL13 | 1 | 416 | G1 | 10G | Dual Path | Sellable | Gen2 | Bare Metal | Live | 50 | 3183936 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 43 | 47 | 0 | 0 | 0 | 0 | 43 | 47 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk417 | DAL13 | 1 | 417 | G1 | 10G | Dual Path | Sellable | Gen2 | Bare Metal | Live | 50 | 3183938 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 41 | 45 | 2 | 0 | 2 | 0 | 43 | 47 | 50 | 47 | 2 | 0 | 49 | 0 | 3 | 1 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk418 | DAL13 | 1 | 418 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3183940 | 20 | 2 | L2 | Z3-375 | 38 |  |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr01.rk419 | DAL13 | 1 | 419 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Build Out | 50 | 3183942 | 20 | 2 | L2 | Z3-375 | 38 | vlam - 4/5/2024 - Allocated to NG for NG2-BAU per DCL-3669 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Build Out | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr01.rk420 | DAL13 | 1 | 420 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 3547025 | 20 | 2 | L2 | Z3-375 | 38 | ysilva - vlam - 2/11/2022 - This has been allocated to NG SAP Rise per DCL-3090. |  | 18 | 21 | 0 | 0 | 0 | 0 | 18 | 21 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.4 | 0.81818 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr01.rk421 | DAL13 | 1 | 421 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3183946 | 20 | 2 | L2 | Z3-375 | 38 | vlam - vlam - 2/11/2022 - This has been allocated to NG SAP Rise per DCL-3090 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | E | 0 | -
dal13.sr01.rk422 | DAL13 | 1 | 422 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441353 | 15 | 2 | L2 | Z6-375 | 39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | S | 0 | -
dal13.sr01.rk423 | DAL13 | 1 | 423 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441355 | 15 | 2 | L2 | Z6-375 | 39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk424 | DAL13 | 1 | 424 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441357 | 15 | 2 | L2 | Z6-375 | 39 |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 2 | 0 | 0 | 2 | 0 | 48 | 48 | 48 | 48 | 0 | 0.3 | 4.3636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk425 | DAL13 | 1 | 425 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441359 | 15 | 2 | L2 | Z5-375 | 39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk426 | DAL13 | 1 | 426 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441361 | 15 | 2 | L2 | Z5-375 | 39 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 32 | 0 | 0 | 32 | 0 | 18 | 18 | 18 | 18 | 0 | 0.3 | 1.6364 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk427 | DAL13 | 1 | 427 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441363 | 15 | 2 | L2 | Z5-375 | 39 | vlam - vlam - 10/12/21 - MAGG & ZER |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.3 | 4.4545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk428 | DAL13 | 1 | 428 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441365 | 15 | 2 | L2 | Z4-375 | 39 | vlam - 11/2/2022 - Allocated to NG for AGG and MAGG |  | 1 | 6 | 0 | 0 | 0 | 0 | 1 | 6 | 50 | 8 | 0 | 0 | 8 | 0 | 42 | 42 | 42 | 42 | 0 | 0.3 | 3.8182 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk429 | DAL13 | 1 | 429 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441367 | 15 | 2 | L2 | Z4-375 | 39 | vlam - 11/2/2022 - Allocated to NG for AGG and MAGG |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.3 | 4.2727 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk430 | DAL13 | 1 | 430 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441369 | 15 | 2 | L2 | Z4-375 | 39 | vlam - 11/2/2022 - Allocated to NG for AGG and MAGG |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.3 | 4.2727 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk431 | DAL13 | 1 | 431 | G1 | 10G | Dual Path | Unsellable | Gen2 | Management | Live | 50 | 1441371 | 15 | 2 | L2 | Z3-375 | 39 | vlam - 11/2/2022 - Allocated to NG for AGG and MAGG |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 5 | 0 | 0 | 5 | 0 | 45 | 45 | 45 | 45 | 0 | 0.3 | 4.0909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr01.rk432 | DAL13 | 1 | 432 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441373 | 15 | 2 | L2 | Z3-375 | 39 | vlam - vlam - 10/12/21 - QZ3 AGG |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Live | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr01.rk433 | DAL13 | 1 | 433 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1441375 | 15 | 2 | L2 | Z3-375 | 39 |  |  | 8 | 12 | 0 | 0 | 0 | 0 | 8 | 12 | 50 | 20 | 0 | 0 | 20 | 0 | 30 | 30 | 30 | 30 | 0 | 0.3 | 2.7273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | E | 0 | -
dal13.sr01.rk434 | DAL13 | 1 | 434 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620965 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 31 | 36 | 2 | 0 | 2 | 0 | 33 | 38 | 57 | 41 | 2 | 0 | 43 | 0 | 16 | 14 | 16 | 16 | 0 | 0.10526 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 2975 | 3599 | 0 | 0 | 6.574 | 0.16034 | 6.8947 |  | -0.89468 | -5.5799 | S | 0 | -
dal13.sr01.rk435 | DAL13 | 1 | 435 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620967 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 29 | 33 | 1 | 0 | 1 | 0 | 30 | 34 | 57 | 38 | 2 | 0 | 40 | 0 | 19 | 17 | 19 | 19 | 0 | 0.10526 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 3001 | 2792 | 0 | 0 | 5.793 | 0.15245 | 6.0979 |  | -0.097895 | -0.64215 | - | 0 | -
dal13.sr01.rk436 | DAL13 | 1 | 436 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620969 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 32 | 37 | 2 | 0 | 2 | 0 | 34 | 39 | 57 | 44 | 3 | 0 | 47 | 0 | 13 | 10 | 13 | 13 | 0 | 0.10526 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 4097 | 3884 | 0 | 0 | 7.981 | 0.18139 | 8.5252 |  | -2.5252 | -13.9214 | - | 0 | -
dal13.sr01.rk437 | DAL13 | 1 | 437 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620971 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 31 | 36 | 3 | 0 | 3 | 0 | 34 | 39 | 57 | 40 | 7 | 0 | 47 | 0 | 17 | 10 | 17 | 17 | 0 | 0.10526 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 3678 | 3559 | 0 | 0 | 7.237 | 0.18093 | 8.5035 |  | -2.5035 | -13.8371 | - | 0 | -
dal13.sr01.rk438 | DAL13 | 1 | 438 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620973 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 21 | 26 | 2 | 0 | 2 | 0 | 23 | 28 | 57 | 39 | 5 | 0 | 44 | 0 | 18 | 13 | 18 | 18 | 0 | 0.10526 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-102 | 2270 | 2424 | 0 | 0 | 4.694 | 0.12036 | 5.2958 |  | 0.70421 | 5.8509 | - | 0 | -
dal13.sr01.rk439 | DAL13 | 1 | 439 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 57 | 1620975 | 5 | 2 | L2 | Z4-375 | 40 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 57 | 4 | 0 | 0 | 4 | 0 | 53 | 53 | 53 | 53 | 0 | 0.087719 | 4.8182 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk440 | DAL13 | 1 | 440 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620977 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 33 | 38 | 2 | 0 | 2 | 0 | 35 | 40 | 57 | 40 | 3 | 0 | 43 | 0 | 17 | 14 | 17 | 17 | 0 | 0.10526 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 4127 | 4119 | 0 | 0 | 8.246 | 0.20615 | 8.8644 |  | -2.8644 | -13.895 | - | 0 | -
dal13.sr01.rk441 | DAL13 | 1 | 441 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620979 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 19 | 24 | 1 | 0 | 1 | 4 | 24 | 29 | 57 | 32 | 1 | 9 | 42 | 0 | 25 | 15 | 16 | 25 | 0 | 0.10526 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 3292 | 3227 | 0 | 0 | 6.519 | 0.20372 | 8.5562 |  | -2.5562 | -12.5476 | - | 0 | -
dal13.sr01.rk442 | DAL13 | 1 | 442 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620981 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 36 | 41 | 0 | 0 | 0 | 1 | 37 | 42 | 57 | 43 | 0 | 1 | 44 | 0 | 14 | 13 | 13 | 14 | 0 | 0.10526 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 4193 | 4627 | 0 | 0 | 8.82 | 0.20512 | 9.0251 |  | -3.0251 | -14.7483 | - | 0 | -
dal13.sr01.rk443 | DAL13 | 1 | 443 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620983 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 38 | 43 | 0 | 0 | 0 | 1 | 39 | 44 | 57 | 45 | 0 | 1 | 46 | 0 | 12 | 11 | 11 | 12 | 0 | 0.10526 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 4342 | 4518 | 0 | 0 | 8.86 | 0.19689 | 9.0569 |  | -3.0569 | -15.526 | - | 0 | -
dal13.sr01.rk444 | DAL13 | 1 | 444 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 57 | 1620985 | 6 | 2 | L2 | Z4-375 | 40 |  |  | 37 | 42 | 2 | 0 | 2 | 0 | 39 | 44 | 57 | 44 | 2 | 0 | 46 | 0 | 13 | 11 | 13 | 13 | 0 | 0.10526 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 4368 | 4316 | 0 | 0 | 8.684 | 0.19736 | 9.0787 |  | -3.0787 | -15.5993 | E | 0 | -
dal13.sr01.rk445 | DAL13 | 1 | 445 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621065 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 30 | 35 | 2 | 0 | 2 | 2 | 34 | 39 | 50 | 39 | 2 | 5 | 46 | 0 | 11 | 4 | 6 | 11 | 0 | 0.12 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-101 | 3804 | 3849 | 0 | 0 | 7.653 | 0.19623 | 9.0266 |  | -3.0266 | -15.4238 | S | 0 | -
dal13.sr01.rk446 | DAL13 | 1 | 446 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621067 | 10 | 2 | L2 | Z4-375 | 41 |  |  | 34 | 39 | 2 | 0 | 2 | 0 | 36 | 41 | 50 | 39 | 2 | 0 | 41 | 0 | 11 | 9 | 11 | 11 | 0 | 0.2 | 1 | 0 | Compute - Live | N | DAL13-101 | 5872 | 6079 | 0 | 0 | 11.951 | 0.30644 | 12.5639 |  | -2.5639 | -8.3667 | - | 0 | -
dal13.sr01.rk447 | DAL13 | 1 | 447 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621069 | 10 | 2 | L2 | Z4-375 | 41 |  |  | 40 | 45 | 0 | 0 | 0 | 1 | 41 | 46 | 50 | 45 | 0 | 1 | 46 | 0 | 5 | 4 | 4 | 5 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-101 | 6783 | 6737 | 0 | 0 | 13.52 | 0.30044 | 13.8204 |  | -3.8204 | -12.716 | - | 0 | -
dal13.sr01.rk448 | DAL13 | 1 | 448 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621071 | 10 | 2 | L2 | Z4-375 | 41 |  |  | 22 | 27 | 8 | 0 | 8 | 0 | 30 | 35 | 50 | 32 | 16 | 0 | 48 | 0 | 18 | 2 | 18 | 18 | 0 | 0.2 | 1.6364 | 0 | Compute - Live | N | DAL13-101 | 3494 | 3398 | 0 | 0 | 6.892 | 0.21538 | 10.338 |  | -0.338 | -1.5694 | - | 0 | -
dal13.sr01.rk449 | DAL13 | 1 | 449 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621073 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 22 | 27 | 5 | 0 | 5 | 2 | 29 | 34 | 50 | 32 | 9 | 2 | 43 | 0 | 18 | 7 | 16 | 18 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 3018 | 2603 | 0 | 0 | 5.621 | 0.17566 | 7.5532 |  | -1.5532 | -8.8424 | - | 0 | -
dal13.sr01.rk450 | DAL13 | 1 | 450 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621075 | 5 | 2 | L2 | Z4-375 | 41 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk451 | DAL13 | 1 | 451 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621077 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 23 | 28 | 6 | 0 | 6 | 4 | 33 | 38 | 50 | 30 | 7 | 5 | 42 | 0 | 20 | 8 | 15 | 20 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 3018 | 3457 | 0 | 0 | 6.475 | 0.21583 | 9.065 |  | -3.065 | -14.2008 | - | 0 | -
dal13.sr01.rk452 | DAL13 | 1 | 452 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621079 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 15 | 20 | 6 | 0 | 6 | 1 | 22 | 27 | 50 | 25 | 11 | 1 | 37 | 0 | 25 | 13 | 24 | 25 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1972 | 1932 | 0 | 0 | 3.904 | 0.15616 | 5.7779 |  | 0.22208 | 1.4221 | - | 0 | -
dal13.sr01.rk453 | DAL13 | 1 | 453 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621081 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 12 | 17 | 8 | 0 | 8 | 2 | 22 | 27 | 50 | 27 | 15 | 5 | 47 | 0 | 23 | 3 | 18 | 23 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2083 | 2074 | 0 | 0 | 4.157 | 0.15396 | 7.2363 |  | -1.2363 | -8.0296 | - | 0 | -
dal13.sr01.rk454 | DAL13 | 1 | 454 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621083 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 12 | 17 | 8 | 0 | 8 | 0 | 20 | 25 | 50 | 26 | 16 | 0 | 42 | 0 | 24 | 8 | 24 | 24 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 1750 | 1752 | 0 | 0 | 3.502 | 0.13469 | 5.6571 |  | 0.34292 | 2.546 | - | 0 | -
dal13.sr01.rk455 | DAL13 | 1 | 455 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621085 | 6 | 2 | L2 | Z4-375 | 41 |  |  | 29 | 34 | 7 | 0 | 7 | 3 | 39 | 44 | 50 | 38 | 7 | 3 | 48 | 0 | 12 | 2 | 9 | 12 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3249 | 3282 | 0 | 0 | 6.531 | 0.17187 | 8.2497 |  | -2.2497 | -13.0896 | E | 0 | -
dal13.sr01.rk456 | DAL13 | 1 | 456 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621087 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 43 | 48 | 0 | 0 | 0 | 0 | 43 | 48 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.2 | 0.18182 | 0 | Compute - Live | N | DAL13-101 | 7912 | 7895 | 0 | 0 | 15.807 | 0.32931 | 15.807 |  | -5.807 | -17.6337 | S | 0 | -
dal13.sr01.rk457 | DAL13 | 1 | 457 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621089 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 43 | 48 | 0 | 0 | 0 | 0 | 43 | 48 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.2 | 0.18182 | 0 | Compute - Live | N | DAL13-101 | 8225 | 7774 | 0 | 0 | 15.999 | 0.33331 | 15.999 |  | -5.999 | -17.9981 | - | 0 | -
dal13.sr01.rk458 | DAL13 | 1 | 458 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621091 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 40 | 45 | 0 | 0 | 0 | 2 | 42 | 47 | 50 | 45 | 0 | 2 | 47 | 0 | 5 | 3 | 3 | 5 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-101 | 7116 | 7055 | 0 | 0 | 14.171 | 0.31491 | 14.8008 |  | -4.8008 | -15.245 | - | 0 | -
dal13.sr01.rk459 | DAL13 | 1 | 459 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621093 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 36 | 41 | 1 | 0 | 1 | 2 | 39 | 44 | 50 | 41 | 1 | 2 | 44 | 0 | 9 | 6 | 7 | 9 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-101 | 5966 | 5966 | 0 | 0 | 11.932 | 0.29102 | 12.8051 |  | -2.8051 | -9.6386 | - | 0 | -
dal13.sr01.rk460 | DAL13 | 1 | 460 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621095 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 39 | 44 | 0 | 0 | 0 | 0 | 39 | 44 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-101 | 5021 | 4770 | 0 | 0 | 9.791 | 0.22252 | 9.791 |  | 0.209 | 0.93923 | - | 0 | -
dal13.sr01.rk461 | DAL13 | 1 | 461 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621097 | 5 | 2 | L2 | Z4-375 | 42 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk462 | DAL13 | 1 | 462 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621099 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 40 | 45 | 1 | 0 | 1 | 0 | 41 | 46 | 50 | 46 | 1 | 0 | 47 | 0 | 4 | 3 | 4 | 4 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-101 | 4636 | 4859 | 0 | 0 | 9.495 | 0.20641 | 9.7014 |  | 0.29859 | 1.4466 | - | 0 | -
dal13.sr01.rk463 | DAL13 | 1 | 463 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621101 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 41 | 46 | 2 | 0 | 2 | 0 | 43 | 48 | 50 | 46 | 2 | 0 | 48 | 0 | 4 | 2 | 4 | 4 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-101 | 5033 | 5091 | 0 | 0 | 10.124 | 0.22009 | 10.5642 |  | -0.56417 | -2.5634 | - | 0 | -
dal13.sr01.rk464 | DAL13 | 1 | 464 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621103 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 29 | 34 | 4 | 0 | 4 | 2 | 35 | 40 | 50 | 37 | 5 | 3 | 45 | 0 | 13 | 5 | 10 | 13 | 0 | 0.2 | 0.90909 | 0 | Compute - Live | N | DAL13-101 | 2421 | 2113 | 0 | 0 | 4.534 | 0.12254 | 5.5143 |  | 4.4857 | 36.6056 | - | 0 | -
dal13.sr01.rk465 | DAL13 | 1 | 465 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621105 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 39 | 44 | 1 | 0 | 1 | 1 | 41 | 46 | 50 | 44 | 1 | 1 | 46 | 0 | 6 | 4 | 5 | 6 | 0 | 0.2 | 0.45455 | 0 | Compute - Live | N | DAL13-101 | 0 | 5153 | 0 | 0 | 5.153 | 0.11711 | 5.3872 | ERROR | 4.6128 | 39.3872 | - | 0 | -
dal13.sr01.rk466 | DAL13 | 1 | 466 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1621107 | 10 | 2 | L2 | Z4-375 | 42 |  |  | 36 | 41 | 0 | 0 | 0 | 0 | 36 | 41 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-101 | 5374 | 4947 | 0 | 0 | 10.321 | 0.23457 | 10.321 |  | -0.321 | -1.3685 | E | 0 | -
dal13.sr01.rk467 | DAL13 | 1 | 467 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621109 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 20 | 25 | 5 | 0 | 5 | 0 | 25 | 30 | 50 | 35 | 9 | 0 | 44 | 0 | 15 | 6 | 15 | 15 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2693 | 2429 | 0 | 0 | 5.122 | 0.14634 | 6.4391 |  | -0.43909 | -3.0004 | S | 0 | -
dal13.sr01.rk468 | DAL13 | 1 | 468 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621111 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 16 | 21 | 4 | 0 | 4 | 3 | 23 | 28 | 50 | 29 | 6 | 6 | 41 | 0 | 21 | 9 | 15 | 21 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2312 | 2246 | 0 | 0 | 4.558 | 0.15717 | 6.4441 |  | -0.44407 | -2.8254 | - | 0 | -
dal13.sr01.rk469 | DAL13 | 1 | 469 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621113 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 24 | 29 | 3 | 0 | 3 | 1 | 28 | 33 | 50 | 35 | 6 | 1 | 42 | 0 | 15 | 8 | 14 | 15 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 3314 | 3131 | 0 | 0 | 6.445 | 0.18414 | 7.734 |  | -1.734 | -9.4166 | - | 0 | -
dal13.sr01.rk470 | DAL13 | 1 | 470 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621115 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 37 | 42 | 0 | 0 | 0 | 1 | 38 | 43 | 50 | 43 | 0 | 1 | 44 | 0 | 7 | 6 | 6 | 7 | 0 | 0.12 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-101 | 0 | 4814 | 0 | 0 | 4.814 | 0.11195 | 4.926 | ERROR | 1.074 | 9.5937 | - | 0 | -
dal13.sr01.rk471 | DAL13 | 1 | 471 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621117 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 35 | 40 | 0 | 0 | 0 | 0 | 35 | 40 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.12 | 0.18182 | 0 | Bare Metal - Live | N | DAL13-101 | 4344 | 4297 | 0 | 0 | 8.641 | 0.18002 | 8.641 |  | -2.641 | -14.6705 | - | 0 | -
dal13.sr01.rk472 | DAL13 | 1 | 472 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621119 | 5 | 2 | L2 | Z5-375 | 43 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk473 | DAL13 | 1 | 473 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621121 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 25 | 30 | 6 | 0 | 6 | 1 | 32 | 37 | 50 | 37 | 10 | 1 | 48 | 0 | 13 | 2 | 12 | 13 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 3565 | 3386 | 0 | 0 | 6.951 | 0.18786 | 9.0175 |  | -3.0175 | -16.0621 | - | 0 | -
dal13.sr01.rk474 | DAL13 | 1 | 474 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621123 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 25 | 30 | 1 | 0 | 1 | 0 | 26 | 31 | 50 | 42 | 1 | 0 | 43 | 0 | 8 | 7 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Bare Metal - Live | N | DAL13-101 | 3825 | 3321 | 0 | 0 | 7.146 | 0.17014 | 7.3161 |  | -1.3161 | -7.7355 | - | 0 | -
dal13.sr01.rk475 | DAL13 | 1 | 475 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621125 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 23 | 28 | 5 | 0 | 5 | 0 | 28 | 33 | 50 | 32 | 13 | 0 | 45 | 0 | 18 | 5 | 18 | 18 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 3116 | 3103 | 0 | 0 | 6.219 | 0.19434 | 8.7455 |  | -2.7455 | -14.1269 | - | 0 | -
dal13.sr01.rk476 | DAL13 | 1 | 476 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621127 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 23 | 28 | 5 | 0 | 5 | 1 | 29 | 34 | 50 | 35 | 8 | 1 | 44 | 0 | 15 | 6 | 14 | 15 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 3027 | 3058 | 0 | 0 | 6.085 | 0.17386 | 7.6497 |  | -1.6497 | -9.4889 | - | 0 | -
dal13.sr01.rk477 | DAL13 | 1 | 477 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621129 | 6 | 2 | L2 | Z5-375 | 43 |  |  | 25 | 30 | 3 | 0 | 3 | 2 | 30 | 35 | 50 | 32 | 3 | 4 | 39 | 0 | 18 | 11 | 14 | 18 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 3523 | 3557 | 0 | 0 | 7.08 | 0.22125 | 8.6288 |  | -2.6288 | -11.8814 | E | 0 | -
dal13.sr01.rk478 | DAL13 | 1 | 478 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621131 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 22 | 27 | 3 | 0 | 3 | 1 | 26 | 31 | 50 | 38 | 5 | 1 | 44 | 0 | 12 | 6 | 11 | 12 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 3473 | 3089 | 0 | 0 | 6.562 | 0.17268 | 7.5981 |  | -1.5981 | -9.2545 | S | 0 | -
dal13.sr01.rk479 | DAL13 | 1 | 479 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621133 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 15 | 20 | 5 | 0 | 5 | 0 | 20 | 25 | 50 | 30 | 15 | 0 | 45 | 0 | 20 | 5 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 2887 | 2851 | 0 | 0 | 5.738 | 0.19127 | 8.607 |  | -2.607 | -13.6302 | - | 0 | -
dal13.sr01.rk480 | DAL13 | 1 | 480 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621135 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 24 | 29 | 2 | 0 | 2 | 1 | 27 | 32 | 50 | 38 | 2 | 8 | 48 | 0 | 12 | 2 | 4 | 12 | 0 | 0.12 | 0.36364 | 0 | Bare Metal - Live | N | DAL13-101 | 3462 | 3376 | 0 | 0 | 6.838 | 0.17995 | 8.6375 |  | -2.6375 | -14.6569 | - | 0 | -
dal13.sr01.rk481 | DAL13 | 1 | 481 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621137 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 18 | 23 | 7 | 0 | 7 | 1 | 26 | 31 | 50 | 25 | 12 | 8 | 45 | 0 | 25 | 5 | 17 | 25 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2258 | 2465 | 0 | 0 | 4.723 | 0.18892 | 8.5014 |  | -2.5014 | -13.2405 | - | 0 | -
dal13.sr01.rk482 | DAL13 | 1 | 482 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621139 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 23 | 28 | 2 | 0 | 2 | 2 | 27 | 32 | 50 | 32 | 4 | 9 | 45 | 0 | 18 | 5 | 9 | 18 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 2837 | 3046 | 0 | 0 | 5.883 | 0.18384 | 8.273 |  | -2.273 | -12.3636 | - | 0 | -
dal13.sr01.rk483 | DAL13 | 1 | 483 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621141 | 5 | 2 | L2 | Z5-375 | 44 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk484 | DAL13 | 1 | 484 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621143 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 24 | 29 | 6 | 0 | 6 | 0 | 30 | 35 | 50 | 35 | 7 | 0 | 42 | 0 | 15 | 8 | 15 | 15 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2901 | 2848 | 0 | 0 | 5.749 | 0.16426 | 6.8988 |  | -0.8988 | -5.4719 | - | 0 | -
dal13.sr01.rk485 | DAL13 | 1 | 485 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621145 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 21 | 26 | 2 | 0 | 2 | 1 | 24 | 29 | 50 | 35 | 3 | 8 | 46 | 0 | 15 | 4 | 7 | 15 | 0 | 0.12 | 0.63636 | 0 | Bare Metal - Live | N | DAL13-101 | 2849 | 3236 | 0 | 0 | 6.085 | 0.17386 | 7.9974 |  | -1.9974 | -11.4889 | - | 0 | -
dal13.sr01.rk486 | DAL13 | 1 | 486 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621147 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 25 | 30 | 3 | 0 | 3 | 1 | 29 | 34 | 50 | 33 | 4 | 2 | 39 | 0 | 17 | 11 | 15 | 17 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 3117 | 3091 | 0 | 0 | 6.208 | 0.18812 | 7.3367 |  | -1.3367 | -7.1057 | - | 0 | -
dal13.sr01.rk487 | DAL13 | 1 | 487 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621149 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 19 | 24 | 5 | 0 | 5 | 2 | 26 | 31 | 50 | 32 | 7 | 9 | 48 | 0 | 18 | 2 | 9 | 18 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3043 | 3170 | 0 | 0 | 6.213 | 0.19416 | 9.3195 |  | -3.3195 | -17.0971 | - | 0 | -
dal13.sr01.rk488 | DAL13 | 1 | 488 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621151 | 6 | 2 | L2 | Z5-375 | 44 |  |  | 17 | 22 | 9 | 0 | 9 | 0 | 26 | 31 | 50 | 33 | 14 | 0 | 47 | 0 | 17 | 3 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2838 | 2613 | 0 | 0 | 5.451 | 0.16518 | 7.7635 |  | -1.7635 | -10.6764 | E | 0 | -
dal13.sr01.rk489 | DAL13 | 1 | 489 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621153 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 38 | 43 | 1 | 0 | 1 | 1 | 40 | 45 | 50 | 45 | 1 | 1 | 47 | 0 | 5 | 3 | 4 | 5 | 0 | 0.12 | 0.36364 | 0 | Bare Metal - Live | N | DAL13-101 | 4554 | 4480 | 0 | 0 | 9.034 | 0.20076 | 9.4355 |  | -3.4355 | -17.1129 | S | 0 | -
dal13.sr01.rk490 | DAL13 | 1 | 490 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621155 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 39 | 44 | 0 | 0 | 0 | 0 | 39 | 44 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-101 | 6084 | 5828 | 0 | 0 | 11.912 | 0.27073 | 11.912 |  | -5.912 | -21.8375 | - | 0 | -
dal13.sr01.rk491 | DAL13 | 1 | 491 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621157 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 19 | 24 | 1 | 0 | 1 | 4 | 24 | 29 | 50 | 29 | 1 | 14 | 44 | 0 | 21 | 6 | 7 | 21 | 0 | 0.12 | 0.63636 | 0 | Bare Metal - Live | N | DAL13-101 | 3153 | 2962 | 0 | 0 | 6.115 | 0.21086 | 9.2779 |  | -3.2779 | -15.5454 | - | 0 | -
dal13.sr01.rk492 | DAL13 | 1 | 492 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621159 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 28 | 33 | 5 | 0 | 5 | 0 | 33 | 38 | 50 | 38 | 6 | 0 | 44 | 0 | 12 | 6 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 3455 | 3357 | 0 | 0 | 6.812 | 0.17926 | 7.8876 |  | -1.8876 | -10.5297 | - | 0 | -
dal13.sr01.rk493 | DAL13 | 1 | 493 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621161 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 18 | 23 | 3 | 0 | 3 | 1 | 22 | 27 | 50 | 33 | 4 | 4 | 41 | 0 | 17 | 9 | 13 | 17 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2557 | 2454 | 0 | 0 | 5.011 | 0.15185 | 6.2258 |  | -0.22579 | -1.4869 | - | 0 | -
dal13.sr01.rk494 | DAL13 | 1 | 494 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621163 | 5 | 2 | L2 | Z6-375 | 45 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk495 | DAL13 | 1 | 495 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621165 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 22 | 27 | 1 | 0 | 1 | 2 | 25 | 30 | 50 | 34 | 2 | 10 | 46 | 0 | 16 | 4 | 6 | 16 | 0 | 0.12 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-101 | 3511 | 3500 | 0 | 0 | 7.011 | 0.20621 | 9.4855 |  | -3.4855 | -16.9029 | - | 0 | -
dal13.sr01.rk496 | DAL13 | 1 | 496 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621167 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 19 | 24 | 1 | 0 | 1 | 0 | 20 | 25 | 50 | 38 | 4 | 0 | 42 | 0 | 12 | 8 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2874 | 2819 | 0 | 0 | 5.693 | 0.14982 | 6.2923 |  | -0.29226 | -1.9508 | - | 0 | -
dal13.sr01.rk497 | DAL13 | 1 | 497 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621169 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 17 | 22 | 3 | 0 | 3 | 1 | 21 | 26 | 50 | 30 | 12 | 2 | 44 | 0 | 20 | 6 | 18 | 20 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2870 | 2741 | 0 | 0 | 5.611 | 0.18703 | 8.2295 |  | -2.2295 | -11.9202 | - | 0 | -
dal13.sr01.rk498 | DAL13 | 1 | 498 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621171 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 20 | 25 | 2 | 0 | 2 | 1 | 23 | 28 | 50 | 33 | 2 | 2 | 37 | 0 | 17 | 13 | 15 | 17 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2622 | 2743 | 0 | 0 | 5.365 | 0.16258 | 6.0153 |  | -0.015303 | -0.094129 | - | 0 | -
dal13.sr01.rk499 | DAL13 | 1 | 499 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621173 | 6 | 2 | L2 | Z6-375 | 45 |  |  | 18 | 23 | 3 | 0 | 3 | 0 | 21 | 26 | 50 | 37 | 5 | 0 | 42 | 0 | 13 | 8 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2704 | 2645 | 0 | 0 | 5.349 | 0.14457 | 6.0718 |  | -0.071838 | -0.49692 | E | 0 | -
dal13.sr01.rk500 | DAL13 | 1 | 500 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621175 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 35 | 40 | 0 | 0 | 0 | 1 | 36 | 41 | 50 | 42 | 0 | 1 | 43 | 0 | 8 | 7 | 7 | 8 | 0 | 0.12 | 0.63636 | 0 | Bare Metal - Live | N | DAL13-102 | 4464 | 4491 | 0 | 0 | 8.955 | 0.21321 | 9.1682 |  | -3.1682 | -14.8593 | S | 0 | -
dal13.sr01.rk501 | DAL13 | 1 | 501 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621177 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 31 | 36 | 2 | 0 | 2 | 1 | 34 | 39 | 50 | 38 | 2 | 2 | 42 | 0 | 12 | 8 | 10 | 12 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-102 | 4122 | 4029 | 0 | 0 | 8.151 | 0.2145 | 9.009 |  | -3.009 | -14.028 | - | 0 | -
dal13.sr01.rk502 | DAL13 | 1 | 502 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621179 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 30 | 35 | 2 | 0 | 2 | 0 | 32 | 37 | 50 | 41 | 3 | 0 | 44 | 0 | 9 | 6 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-102 | 3581 | 3526 | 0 | 0 | 7.107 | 0.17334 | 7.627 |  | -1.627 | -9.3862 | - | 0 | -
dal13.sr01.rk503 | DAL13 | 1 | 503 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621181 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 24 | 29 | 2 | 0 | 2 | 2 | 28 | 33 | 50 | 33 | 4 | 2 | 39 | 0 | 17 | 11 | 15 | 17 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 3329 | 3279 | 0 | 0 | 6.608 | 0.20024 | 7.8095 |  | -1.8095 | -9.0363 | - | 0 | -
dal13.sr01.rk504 | DAL13 | 1 | 504 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621183 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 35 | 40 | 2 | 0 | 2 | 2 | 39 | 44 | 50 | 41 | 3 | 2 | 46 | 0 | 9 | 4 | 7 | 9 | 0 | 0.12 | 0.63636 | 0 | Bare Metal - Live | N | DAL13-102 | 4051 | 4088 | 0 | 0 | 8.139 | 0.19851 | 9.1316 |  | -3.1316 | -15.7752 | - | 0 | -
dal13.sr01.rk505 | DAL13 | 1 | 505 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621185 | 5 | 2 | L2 | Z5-375 | 46 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk506 | DAL13 | 1 | 506 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621187 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 27 | 32 | 4 | 0 | 4 | 0 | 31 | 36 | 50 | 37 | 4 | 0 | 41 | 0 | 13 | 9 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3186 | 3150 | 0 | 0 | 6.336 | 0.17124 | 7.021 |  | -1.021 | -5.9621 | - | 0 | -
dal13.sr01.rk507 | DAL13 | 1 | 507 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621189 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 28 | 33 | 4 | 0 | 4 | 0 | 32 | 37 | 50 | 38 | 4 | 0 | 42 | 0 | 12 | 8 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-102 | 3240 | 3042 | 0 | 0 | 6.282 | 0.16532 | 6.9433 |  | -0.94326 | -5.7058 | - | 0 | -
dal13.sr01.rk508 | DAL13 | 1 | 508 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621191 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 28 | 33 | 2 | 0 | 2 | 0 | 30 | 35 | 50 | 35 | 3 | 0 | 38 | 0 | 15 | 12 | 15 | 15 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 2924 | 3882 | 0 | 0 | 6.806 | 0.19446 | 7.3894 |  | -1.3894 | -7.1449 | - | 0 | -
dal13.sr01.rk509 | DAL13 | 1 | 509 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621193 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 33 | 38 | 0 | 0 | 0 | 1 | 34 | 39 | 50 | 38 | 0 | 1 | 39 | 0 | 12 | 11 | 11 | 12 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 4595 | 3485 | 0 | 0 | 8.08 | 0.21263 | 8.2926 |  | -2.2926 | -10.7822 | - | 0 | -
dal13.sr01.rk510 | DAL13 | 1 | 510 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621195 | 6 | 2 | L2 | Z5-375 | 46 |  |  | 39 | 44 | 0 | 0 | 0 | 1 | 40 | 45 | 50 | 44 | 0 | 1 | 45 | 0 | 6 | 5 | 5 | 6 | 0 | 0.12 | 0.45455 | 0 | Bare Metal - Live | N | DAL13-102 | 4444 | 5825 | 0 | 0 | 10.269 | 0.23339 | 10.5024 |  | -4.5024 | -19.2916 | E | 0 | -
dal13.sr01.rk511 | DAL13 | 1 | 511 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621197 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 33 | 38 | 0 | 0 | 0 | 0 | 33 | 38 | 50 | 38 | 0 | 0 | 38 | 0 | 12 | 12 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 4063 | 4269 | 0 | 0 | 8.332 | 0.21926 | 8.332 |  | -2.332 | -10.6356 | S | 0 | -
dal13.sr01.rk512 | DAL13 | 1 | 512 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621199 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 37 | 42 | 0 | 0 | 0 | 1 | 38 | 43 | 50 | 42 | 0 | 1 | 43 | 0 | 8 | 7 | 7 | 8 | 0 | 0.12 | 0.63636 | 0 | Bare Metal - Live | N | DAL13-101 | 5659 | 5628 | 0 | 0 | 11.287 | 0.26874 | 11.5557 |  | -5.5557 | -20.6734 | - | 0 | -
dal13.sr01.rk513 | DAL13 | 1 | 513 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621201 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 35 | 40 | 0 | 0 | 0 | 0 | 35 | 40 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.12 | 0.27273 | 0 | Bare Metal - Live | N | DAL13-101 | 5117 | 3383 | 0 | 0 | 8.5 | 0.18085 | 8.5 |  | -2.5 | -13.8235 | - | 0 | -
dal13.sr01.rk514 | DAL13 | 1 | 514 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621203 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 29 | 34 | 7 | 0 | 7 | 0 | 36 | 41 | 50 | 39 | 8 | 0 | 47 | 0 | 11 | 3 | 11 | 11 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 3456 | 3289 | 0 | 0 | 6.745 | 0.17295 | 8.1286 |  | -2.1286 | -12.3076 | - | 0 | -
dal13.sr01.rk515 | DAL13 | 1 | 515 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621205 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 28 | 33 | 1 | 0 | 1 | 1 | 30 | 35 | 50 | 36 | 2 | 1 | 39 | 0 | 14 | 11 | 13 | 14 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 4081 | 4098 | 0 | 0 | 8.179 | 0.22719 | 8.8606 |  | -2.8606 | -12.5909 | - | 0 | -
dal13.sr01.rk516 | DAL13 | 1 | 516 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1621207 | 5 | 2 | L2 | Z6-375 | 47 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr01.rk517 | DAL13 | 1 | 517 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621209 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 31 | 36 | 3 | 0 | 3 | 0 | 34 | 39 | 50 | 42 | 3 | 0 | 45 | 0 | 8 | 5 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Bare Metal - Live | N | DAL13-101 | 3394 | 3343 | 0 | 0 | 6.737 | 0.1604 | 7.2182 |  | -1.2182 | -7.5946 | - | 0 | -
dal13.sr01.rk518 | DAL13 | 1 | 518 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621211 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 23 | 28 | 15 | 0 | 15 | 0 | 38 | 43 | 50 | 28 | 15 | 0 | 43 | 0 | 22 | 7 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2802 | 3052 | 0 | 0 | 5.854 | 0.20907 | 8.9901 |  | -2.9901 | -14.3017 | - | 0 | -
dal13.sr01.rk519 | DAL13 | 1 | 519 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621213 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 21 | 26 | 8 | 0 | 8 | 1 | 30 | 35 | 50 | 33 | 8 | 2 | 43 | 0 | 17 | 7 | 15 | 17 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2292 | 3052 | 0 | 0 | 5.344 | 0.16194 | 6.9634 |  | -0.96339 | -5.9491 | - | 0 | -
dal13.sr01.rk520 | DAL13 | 1 | 520 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621215 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 25 | 30 | 4 | 0 | 4 | 1 | 30 | 35 | 50 | 38 | 6 | 1 | 45 | 0 | 12 | 5 | 11 | 12 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 3388 | 3359 | 0 | 0 | 6.747 | 0.17755 | 7.9899 |  | -1.9899 | -11.2072 | - | 0 | -
dal13.sr01.rk521 | DAL13 | 1 | 521 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1621217 | 6 | 2 | L2 | Z6-375 | 47 |  |  | 27 | 32 | 3 | 0 | 3 | 1 | 31 | 36 | 50 | 36 | 4 | 2 | 42 | 0 | 14 | 8 | 12 | 14 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2755 | 2946 | 0 | 0 | 5.701 | 0.15836 | 6.6512 |  | -0.65117 | -4.1119 | E | 0 | -
dal13.sr01.rk522 | DAL13 | 1 | 522 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621219 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 15 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | S | 0 | -
dal13.sr01.rk523 | DAL13 | 1 | 523 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621221 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 11 | 15 | 0 | 0 | 0 | 0 | 11 | 15 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk524 | DAL13 | 1 | 524 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621223 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 9 | 15 | 0 | 0 | 0 | 0 | 9 | 15 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.12 | 0.45455 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk525 | DAL13 | 1 | 525 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621225 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 11 | 14 | 0 | 0 | 0 | 0 | 11 | 14 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk526 | DAL13 | 1 | 526 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621227 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 13 | 15 | 0 | 0 | 0 | 0 | 13 | 15 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk527 | DAL13 | 1 | 527 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621229 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 14 | 16 | 0 | 0 | 0 | 0 | 14 | 16 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk528 | DAL13 | 1 | 528 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621231 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 13 | 14 | 0 | 0 | 0 | 0 | 13 | 14 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk529 | DAL13 | 1 | 529 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621233 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 11 | 14 | 0 | 0 | 0 | 0 | 11 | 14 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk530 | DAL13 | 1 | 530 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621235 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 9 | 15 | 0 | 0 | 0 | 0 | 9 | 15 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.12 | 0.45455 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk531 | DAL13 | 1 | 531 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621237 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 11 | 15 | 0 | 0 | 0 | 0 | 11 | 15 | 50 | 44 | 0 | 0 | 44 | 0 | 6 | 6 | 6 | 6 | 0 | 0.12 | 0.54545 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr01.rk532 | DAL13 | 1 | 532 | 1 | 10G | Dual Path | Sellable | Storage | COS | Live | 50 | 1621239 | 6 | 2 | L2 | Z6-375 | 48 | vlam - Per Andy, assigned to COS on 10/31/19. |  | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 15 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.12 | 0.72727 | 0 | Storage - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | E | 0 | -
dal13.sr02.rk533 | DAL13 | 2 | 533 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382893 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 24 | 29 | 1 | 0 | 1 | 2 | 27 | 32 | 50 | 37 | 4 | 4 | 45 | 0 | 13 | 5 | 9 | 13 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3094 | 2646 | 0 | 0 | 5.74 | 0.15514 | 6.9811 |  | -0.98108 | -6.324 | S | 0 | -
dal13.sr02.rk534 | DAL13 | 2 | 534 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382895 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 21 | 26 | 4 | 0 | 4 | 2 | 27 | 32 | 50 | 32 | 4 | 3 | 39 | 0 | 18 | 11 | 15 | 18 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2642 | 2583 | 0 | 0 | 5.225 | 0.16328 | 6.368 |  | -0.36797 | -2.2536 | - | 0 | -
dal13.sr02.rk535 | DAL13 | 2 | 535 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382897 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 26 | 31 | 4 | 0 | 4 | 0 | 30 | 35 | 50 | 41 | 5 | 0 | 46 | 0 | 9 | 4 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3308 | 3277 | 0 | 0 | 6.585 | 0.16061 | 7.388 |  | -1.388 | -8.6424 | - | 0 | -
dal13.sr02.rk536 | DAL13 | 2 | 536 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382899 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 26 | 31 | 4 | 0 | 4 | 2 | 32 | 37 | 50 | 34 | 7 | 3 | 44 | 0 | 16 | 6 | 13 | 16 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 3914 | 3666 | 0 | 0 | 7.58 | 0.22294 | 9.8094 |  | -3.8094 | -17.0871 | - | 0 | -
dal13.sr02.rk537 | DAL13 | 2 | 537 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382901 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 24 | 29 | 4 | 0 | 4 | 1 | 29 | 34 | 50 | 35 | 8 | 2 | 45 | 0 | 15 | 5 | 13 | 15 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 3402 | 3172 | 0 | 0 | 6.574 | 0.18783 | 8.4523 |  | -2.4523 | -13.056 | - | 0 | -
dal13.sr02.rk538 | DAL13 | 2 | 538 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1382903 | 5 | 3 | L3 | Z1-375 | 1 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk539 | DAL13 | 2 | 539 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382905 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 18 | 23 | 7 | 0 | 7 | 2 | 27 | 32 | 50 | 25 | 8 | 9 | 42 | 0 | 25 | 8 | 16 | 25 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2477 | 2390 | 0 | 0 | 4.867 | 0.19468 | 8.1766 |  | -2.1766 | -11.1802 | - | 0 | -
dal13.sr02.rk540 | DAL13 | 2 | 540 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382907 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 22 | 27 | 1 | 0 | 1 | 2 | 25 | 30 | 50 | 35 | 1 | 6 | 42 | 0 | 15 | 8 | 9 | 15 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3021 | 2953 | 0 | 0 | 5.974 | 0.17069 | 7.1688 |  | -1.1688 | -6.8477 | - | 0 | -
dal13.sr02.rk541 | DAL13 | 2 | 541 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382909 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 22 | 27 | 2 | 0 | 2 | 1 | 25 | 30 | 50 | 34 | 2 | 8 | 44 | 0 | 16 | 6 | 8 | 16 | 0 | 0.12 | 0.72727 | 0 | Bare Metal - Live | N | DAL13-101 | 3036 | 2923 | 0 | 0 | 5.959 | 0.17526 | 7.7116 |  | -1.7116 | -9.7661 | - | 0 | -
dal13.sr02.rk542 | DAL13 | 2 | 542 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382911 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 22 | 27 | 5 | 0 | 5 | 1 | 28 | 33 | 50 | 30 | 14 | 1 | 45 | 0 | 20 | 5 | 19 | 20 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 3466 | 3535 | 0 | 0 | 7.001 | 0.23337 | 10.5015 |  | -4.5015 | -19.2894 | - | 0 | -
dal13.sr02.rk543 | DAL13 | 2 | 543 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382913 | 6 | 3 | L3 | Z1-375 | 1 |  |  | 22 | 27 | 6 | 0 | 6 | 0 | 28 | 33 | 50 | 30 | 11 | 0 | 41 | 0 | 20 | 9 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 2752 | 2626 | 0 | 0 | 5.378 | 0.17927 | 7.3499 |  | -1.3499 | -7.5303 | E | 0 | -
dal13.sr02.rk544 | DAL13 | 2 | 544 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382915 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 22 | 27 | 2 | 0 | 2 | 0 | 24 | 29 | 50 | 35 | 3 | 0 | 38 | 0 | 15 | 12 | 15 | 15 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2906 | 0 | 0 | 0 | 2.906 | 0.083029 | 3.1551 | ERROR | 2.8449 | 34.2643 | S | 0 | -
dal13.sr02.rk545 | DAL13 | 2 | 545 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382917 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 20 | 25 | 4 | 0 | 4 | 1 | 25 | 30 | 50 | 34 | 8 | 1 | 43 | 0 | 16 | 7 | 15 | 16 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 2594 | 2683 | 0 | 0 | 5.277 | 0.15521 | 6.6739 |  | -0.67385 | -4.3417 | - | 0 | -
dal13.sr02.rk546 | DAL13 | 2 | 546 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382919 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 22 | 27 | 0 | 0 | 0 | 1 | 23 | 28 | 50 | 41 | 0 | 1 | 42 | 0 | 9 | 8 | 8 | 9 | 0 | 0.12 | 0.72727 | 0 | Bare Metal - Live | N | DAL13-101 | 3813 | 3783 | 0 | 0 | 7.596 | 0.18527 | 7.7813 |  | -1.7813 | -9.6145 | - | 0 | -
dal13.sr02.rk547 | DAL13 | 2 | 547 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382921 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 25 | 30 | 1 | 0 | 1 | 2 | 28 | 33 | 50 | 36 | 1 | 9 | 46 | 0 | 14 | 4 | 5 | 14 | 0 | 0.12 | 0.45455 | 0 | Bare Metal - Live | N | DAL13-101 | 3054 | 3153 | 0 | 0 | 6.207 | 0.17242 | 7.9312 |  | -1.9312 | -11.2006 | - | 0 | -
dal13.sr02.rk548 | DAL13 | 2 | 548 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382923 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 15 | 20 | 2 | 0 | 2 | 2 | 19 | 24 | 50 | 26 | 9 | 9 | 44 | 0 | 24 | 6 | 15 | 24 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 1997 | 1937 | 0 | 0 | 3.934 | 0.15131 | 6.6575 |  | -0.65754 | -4.3457 | - | 0 | -
dal13.sr02.rk549 | DAL13 | 2 | 549 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1382925 | 5 | 3 | L3 | Z1-375 | 2 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk550 | DAL13 | 2 | 550 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382927 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 17 | 22 | 8 | 0 | 8 | 2 | 27 | 32 | 50 | 27 | 10 | 9 | 46 | 0 | 23 | 4 | 14 | 23 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2455 | 2388 | 0 | 0 | 4.843 | 0.17937 | 8.251 |  | -2.251 | -12.5497 | - | 0 | -
dal13.sr02.rk551 | DAL13 | 2 | 551 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382993 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 20 | 25 | 3 | 0 | 3 | 3 | 26 | 31 | 50 | 31 | 4 | 10 | 45 | 0 | 19 | 5 | 9 | 19 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 2654 | 2694 | 0 | 0 | 5.348 | 0.17252 | 7.7632 |  | -1.7632 | -10.2206 | - | 0 | -
dal13.sr02.rk552 | DAL13 | 2 | 552 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382995 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 23 | 28 | 6 | 0 | 6 | 1 | 30 | 35 | 50 | 30 | 7 | 8 | 45 | 0 | 20 | 5 | 12 | 20 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2885 | 2636 | 0 | 0 | 5.521 | 0.18403 | 8.2815 |  | -2.2815 | -12.3972 | - | 0 | -
dal13.sr02.rk553 | DAL13 | 2 | 553 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382997 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 17 | 22 | 6 | 0 | 6 | 5 | 28 | 33 | 50 | 26 | 7 | 12 | 45 | 0 | 24 | 5 | 12 | 24 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 0 | 2540 | 0 | 0 | 2.54 | 0.097692 | 4.3962 | ERROR | 1.6038 | 16.4173 | - | 0 | -
dal13.sr02.rk554 | DAL13 | 2 | 554 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382999 | 6 | 3 | L3 | Z1-375 | 2 |  |  | 23 | 28 | 6 | 0 | 6 | 2 | 31 | 36 | 50 | 28 | 8 | 9 | 45 | 0 | 22 | 5 | 13 | 22 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2971 | 2982 | 0 | 0 | 5.953 | 0.21261 | 9.5673 |  | -3.5673 | -16.7789 | E | 0 | -
dal13.sr02.rk555 | DAL13 | 2 | 555 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383001 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 19 | 24 | 3 | 0 | 3 | 0 | 22 | 27 | 50 | 42 | 5 | 0 | 47 | 0 | 8 | 3 | 8 | 8 | 0 | 0.2 | 0.72727 | 0 | Compute - Live | N | DAL13-101 | 3158 | 2874 | 0 | 0 | 6.032 | 0.14362 | 6.7501 |  | 3.2499 | 22.6286 | S | 0 | -
dal13.sr02.rk556 | DAL13 | 2 | 556 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383003 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 15 | 20 | 2 | 0 | 2 | 1 | 18 | 23 | 50 | 35 | 4 | 8 | 47 | 0 | 15 | 3 | 7 | 15 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-101 | 3084 | 1842 | 0 | 0 | 4.926 | 0.14074 | 6.6149 |  | 3.3851 | 24.0516 | - | 0 | -
dal13.sr02.rk557 | DAL13 | 2 | 557 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383005 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 21 | 26 | 0 | 0 | 0 | 2 | 23 | 28 | 50 | 41 | 0 | 6 | 47 | 0 | 9 | 3 | 3 | 9 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-101 | 3766 | 2185 | 0 | 0 | 5.951 | 0.14515 | 6.8219 |  | 3.1781 | 21.896 | - | 0 | -
dal13.sr02.rk558 | DAL13 | 2 | 558 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383007 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 20 | 25 | 4 | 0 | 4 | 0 | 24 | 29 | 50 | 39 | 7 | 0 | 46 | 0 | 11 | 4 | 11 | 11 | 0 | 0.2 | 1 | 0 | Compute - Live | N | DAL13-101 | 3410 | 2536 | 0 | 0 | 5.946 | 0.15246 | 7.0132 |  | 2.9868 | 19.5903 | - | 0 | -
dal13.sr02.rk559 | DAL13 | 2 | 559 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383009 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 20 | 25 | 0 | 0 | 0 | 0 | 20 | 25 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.2 | 0.45455 | 0 | Compute - Live | N | DAL13-101 | 2917 | 3266 | 0 | 0 | 6.183 | 0.1374 | 6.183 |  | 3.817 | 27.7802 | - | 0 | -
dal13.sr02.rk560 | DAL13 | 2 | 560 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383011 | 5 | 3 | L3 | Z1-375 | 3 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk561 | DAL13 | 2 | 561 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383013 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 23 | 28 | 2 | 0 | 2 | 1 | 26 | 31 | 50 | 42 | 4 | 2 | 48 | 0 | 8 | 2 | 6 | 8 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-101 | 3536 | 2712 | 0 | 0 | 6.248 | 0.14876 | 7.1406 |  | 2.8594 | 19.2215 | - | 0 | -
dal13.sr02.rk562 | DAL13 | 2 | 562 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383015 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 21 | 26 | 1 | 0 | 1 | 0 | 22 | 27 | 50 | 46 | 2 | 0 | 48 | 0 | 4 | 2 | 4 | 4 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-101 | 3513 | 2660 | 0 | 0 | 6.173 | 0.1342 | 6.4414 |  | 3.5586 | 26.5181 | - | 0 | -
dal13.sr02.rk563 | DAL13 | 2 | 563 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383017 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 16 | 21 | 1 | 0 | 1 | 1 | 18 | 23 | 50 | 35 | 4 | 8 | 47 | 0 | 15 | 3 | 7 | 15 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-101 | 2418 | 2384 | 0 | 0 | 4.802 | 0.1372 | 6.4484 |  | 3.5516 | 25.8863 | - | 0 | -
dal13.sr02.rk564 | DAL13 | 2 | 564 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383019 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 21 | 26 | 5 | 0 | 5 | 1 | 27 | 32 | 50 | 40 | 6 | 2 | 48 | 0 | 10 | 2 | 8 | 10 | 0 | 0.2 | 0.72727 | 0 | Compute - Live | N | DAL13-101 | 2658 | 3403 | 0 | 0 | 6.061 | 0.15152 | 7.2732 |  | 2.7268 | 17.9957 | - | 0 | -
dal13.sr02.rk565 | DAL13 | 2 | 565 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383021 | 10 | 3 | L3 | Z1-375 | 3 |  |  | 18 | 23 | 2 | 0 | 2 | 0 | 20 | 25 | 50 | 42 | 6 | 0 | 48 | 0 | 8 | 2 | 8 | 8 | 0 | 0.2 | 0.72727 | 0 | Compute - Live | N | DAL13-101 | 3328 | 2784 | 0 | 0 | 6.112 | 0.14552 | 6.9851 |  | 3.0149 | 20.7173 | E | 0 | -
dal13.sr02.rk566 | DAL13 | 2 | 566 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383023 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 23 | 28 | 0 | 0 | 0 | 0 | 23 | 28 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-101 | 2167 | 4330 | 0 | 0 | 6.497 | 0.13823 | 6.497 |  | 3.503 | 25.3411 | S | 0 | -
dal13.sr02.rk567 | DAL13 | 2 | 567 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383025 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 23 | 28 | 1 | 0 | 1 | 1 | 25 | 30 | 50 | 43 | 2 | 1 | 46 | 0 | 7 | 4 | 6 | 7 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-101 | 2570 | 4190 | 0 | 0 | 6.76 | 0.15721 | 7.2316 |  | 2.7684 | 17.6095 | - | 0 | -
dal13.sr02.rk568 | DAL13 | 2 | 568 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383027 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 18 | 23 | 0 | 0 | 0 | 0 | 18 | 23 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.2 | 0.45455 | 0 | Compute - Live | N | DAL13-101 | 2827 | 2625 | 0 | 0 | 5.452 | 0.12116 | 5.452 |  | 4.548 | 37.5385 | - | 0 | -
dal13.sr02.rk569 | DAL13 | 2 | 569 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383029 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 19 | 24 | 0 | 0 | 0 | 1 | 20 | 25 | 50 | 40 | 0 | 8 | 48 | 0 | 10 | 2 | 2 | 10 | 0 | 0.2 | 0.18182 | 0 | Compute - Live | N | DAL13-101 | 2639 | 3557 | 0 | 0 | 6.196 | 0.1549 | 7.4352 |  | 2.5648 | 16.5578 | - | 0 | -
dal13.sr02.rk570 | DAL13 | 2 | 570 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383031 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 20 | 25 | 0 | 0 | 0 | 1 | 21 | 26 | 50 | 40 | 0 | 8 | 48 | 0 | 10 | 2 | 2 | 10 | 0 | 0.2 | 0.18182 | 0 | Compute - Live | N | DAL13-101 | 3388 | 2265 | 0 | 0 | 5.653 | 0.14132 | 6.7836 |  | 3.2164 | 22.7589 | - | 0 | -
dal13.sr02.rk571 | DAL13 | 2 | 571 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383033 | 5 | 3 | L3 | Z2-375 | 4 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk572 | DAL13 | 2 | 572 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383035 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 16 | 21 | 2 | 0 | 2 | 0 | 18 | 23 | 50 | 42 | 4 | 0 | 46 | 0 | 8 | 4 | 8 | 8 | 0 | 0.2 | 0.72727 | 0 | Compute - Live | N | DAL13-101 | 3134 | 2015 | 0 | 0 | 5.149 | 0.1226 | 5.6394 |  | 4.3606 | 35.5692 | - | 0 | -
dal13.sr02.rk573 | DAL13 | 2 | 573 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383037 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 18 | 23 | 1 | 0 | 1 | 0 | 19 | 24 | 50 | 43 | 1 | 0 | 44 | 0 | 7 | 6 | 7 | 7 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-101 | 3325 | 2296 | 0 | 0 | 5.621 | 0.13072 | 5.7517 |  | 4.2483 | 32.4988 | - | 0 | -
dal13.sr02.rk574 | DAL13 | 2 | 574 | 1 | 10G | Dual Path | Sellable | Compute | vGPU | Live | 50 | 1383039 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 21 | 26 | 1 | 0 | 1 | 1 | 23 | 28 | 50 | 44 | 2 | 2 | 48 | 0 | 6 | 2 | 4 | 6 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-101 | 4213 | 2583 | 0 | 0 | 6.796 | 0.15445 | 7.4138 |  | 2.5862 | 16.744 | - | 0 | -
dal13.sr02.rk575 | DAL13 | 2 | 575 | 1 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383041 | 10 | 3 | L3 | Z2-375 | 4 |  |  | 22 | 27 | 1 | 0 | 1 | 0 | 23 | 28 | 50 | 41 | 4 | 0 | 45 | 0 | 9 | 5 | 9 | 9 | 0 | 0.2 | 0.81818 | 0 | Compute - Live | N | DAL13-101 | 3216 | 2936 | 0 | 0 | 6.152 | 0.15005 | 6.7522 |  | 3.2478 | 21.645 | - | 0 | -
dal13.sr02.rk576 | DAL13 | 2 | 576 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383043 | 6 | 3 | L3 | Z2-375 | 4 |  |  | 22 | 27 | 3 | 0 | 3 | 0 | 25 | 30 | 50 | 40 | 6 | 0 | 46 | 0 | 10 | 4 | 10 | 10 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-101 | 3138 | 3222 | 0 | 0 | 6.36 | 0.159 | 7.314 |  | -1.314 | -8.2642 | E | 0 | -
dal13.sr02.rk577 | DAL13 | 2 | 577 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383045 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 21 | 26 | 6 | 0 | 6 | 0 | 27 | 32 | 50 | 34 | 12 | 0 | 46 | 0 | 16 | 4 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2641 | 2627 | 0 | 0 | 5.268 | 0.15494 | 7.1273 |  | -1.1273 | -7.2756 | S | 0 | -
dal13.sr02.rk578 | DAL13 | 2 | 578 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383047 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 15 | 20 | 3 | 0 | 3 | 0 | 18 | 23 | 50 | 28 | 4 | 0 | 32 | 0 | 22 | 18 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-101 | 2385 | 2325 | 0 | 0 | 4.71 | 0.16821 | 5.3829 |  | 0.61714 | 3.6688 | - | 0 | -
dal13.sr02.rk579 | DAL13 | 2 | 579 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383049 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 22 | 27 | 11 | 0 | 11 | 0 | 33 | 38 | 50 | 33 | 13 | 0 | 46 | 0 | 17 | 4 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 3633 | 3474 | 0 | 0 | 7.107 | 0.21536 | 9.9067 |  | -3.9067 | -18.1401 | - | 0 | -
dal13.sr02.rk580 | DAL13 | 2 | 580 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383051 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 22 | 27 | 9 | 0 | 9 | 1 | 32 | 37 | 50 | 34 | 10 | 1 | 45 | 0 | 16 | 5 | 15 | 16 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-101 | 3258 | 3264 | 0 | 0 | 6.522 | 0.19182 | 8.6321 |  | -2.6321 | -13.7213 | - | 0 | -
dal13.sr02.rk581 | DAL13 | 2 | 581 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383053 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 23 | 28 | 4 | 0 | 4 | 1 | 28 | 33 | 50 | 31 | 12 | 1 | 44 | 0 | 19 | 6 | 18 | 19 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 4396 | 4266 | 0 | 0 | 8.662 | 0.27942 | 12.2945 |  | -6.2945 | -22.5269 | - | 0 | -
dal13.sr02.rk582 | DAL13 | 2 | 582 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383055 | 5 | 3 | L3 | Z2-375 | 5 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk583 | DAL13 | 2 | 583 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383057 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 23 | 28 | 4 | 0 | 4 | 2 | 29 | 34 | 50 | 32 | 4 | 9 | 45 | 0 | 18 | 5 | 9 | 18 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-101 | 3602 | 3097 | 0 | 0 | 6.699 | 0.20934 | 9.4205 |  | -3.4205 | -16.339 | - | 0 | -
dal13.sr02.rk584 | DAL13 | 2 | 584 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383059 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 21 | 26 | 4 | 0 | 4 | 5 | 30 | 35 | 50 | 34 | 5 | 5 | 44 | 0 | 16 | 6 | 11 | 16 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-101 | 2502 | 3346 | 0 | 0 | 5.848 | 0.172 | 7.568 |  | -1.568 | -9.1163 | - | 0 | -
dal13.sr02.rk585 | DAL13 | 2 | 585 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383061 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 12 | 17 | 13 | 0 | 13 | 0 | 25 | 30 | 50 | 19 | 23 | 0 | 42 | 0 | 31 | 8 | 31 | 31 | 0 | 0.12 | 2.8182 | 0 | Bare Metal - Live | N | DAL13-101 | 1538 | 1489 | 0 | 0 | 3.027 | 0.15932 | 6.6913 |  | -0.69126 | -4.3389 | - | 0 | -
dal13.sr02.rk586 | DAL13 | 2 | 586 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383063 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 11 | 16 | 11 | 0 | 11 | 1 | 23 | 28 | 50 | 19 | 22 | 1 | 42 | 0 | 31 | 8 | 30 | 31 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-101 | 1789 | 1742 | 0 | 0 | 3.531 | 0.18584 | 7.8054 |  | -1.8054 | -9.7145 | - | 0 | -
dal13.sr02.rk587 | DAL13 | 2 | 587 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383065 | 6 | 3 | L3 | Z2-375 | 5 |  |  | 23 | 28 | 3 | 0 | 3 | 0 | 26 | 31 | 50 | 38 | 6 | 0 | 44 | 0 | 12 | 6 | 12 | 12 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 2595 | 2895 | 0 | 0 | 5.49 | 0.14447 | 6.3568 |  | -0.35684 | -2.4699 | E | 0 | -
dal13.sr02.rk588 | DAL13 | 2 | 588 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383067 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 19 | 24 | 3 | 0 | 3 | 0 | 22 | 27 | 50 | 37 | 7 | 0 | 44 | 0 | 13 | 6 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-101 | 2684 | 2619 | 0 | 0 | 5.303 | 0.14332 | 6.3063 |  | -0.30627 | -2.1369 | S | 0 | -
dal13.sr02.rk589 | DAL13 | 2 | 589 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383069 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 21 | 26 | 7 | 0 | 7 | 1 | 29 | 34 | 50 | 36 | 8 | 2 | 46 | 0 | 14 | 4 | 12 | 14 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 3449 | 3315 | 0 | 0 | 6.764 | 0.18789 | 8.6429 |  | -2.6429 | -14.0662 | - | 0 | -
dal13.sr02.rk590 | DAL13 | 2 | 590 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383071 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 19 | 24 | 9 | 0 | 9 | 2 | 30 | 35 | 50 | 27 | 14 | 2 | 43 | 0 | 23 | 7 | 21 | 23 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 3160 | 2747 | 0 | 0 | 5.907 | 0.21878 | 9.4074 |  | -3.4074 | -15.5749 | - | 0 | -
dal13.sr02.rk591 | DAL13 | 2 | 591 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383073 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 22 | 27 | 4 | 0 | 4 | 0 | 26 | 31 | 50 | 36 | 6 | 0 | 42 | 0 | 14 | 8 | 14 | 14 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2331 | 2251 | 0 | 0 | 4.582 | 0.12728 | 5.3457 |  | 0.65433 | 5.141 | - | 0 | -
dal13.sr02.rk592 | DAL13 | 2 | 592 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383075 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 17 | 22 | 1 | 0 | 1 | 4 | 22 | 27 | 50 | 34 | 2 | 4 | 40 | 0 | 16 | 10 | 12 | 16 | 0 | 0.12 | 1.0909 | 0 | Bare Metal - Live | N | DAL13-101 | 1919 | 1886 | 0 | 0 | 3.805 | 0.11191 | 4.4765 |  | 1.5235 | 13.6137 | - | 0 | -
dal13.sr02.rk593 | DAL13 | 2 | 593 | 1 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383077 | 5 | 3 | L3 | Z2-375 | 6 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk594 | DAL13 | 2 | 594 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383079 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 13 | 18 | 7 | 0 | 7 | 1 | 21 | 26 | 50 | 24 | 13 | 8 | 45 | 0 | 26 | 5 | 18 | 26 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-101 | 2500 | 2250 | 0 | 0 | 4.75 | 0.19792 | 8.9062 |  | -2.9062 | -14.6842 | - | 0 | -
dal13.sr02.rk595 | DAL13 | 2 | 595 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383081 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 24 | 29 | 4 | 0 | 4 | 0 | 28 | 33 | 50 | 34 | 12 | 0 | 46 | 0 | 16 | 4 | 16 | 16 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-101 | 2888 | 2543 | 0 | 0 | 5.431 | 0.15974 | 7.3478 |  | -1.3478 | -8.4379 | - | 0 | -
dal13.sr02.rk596 | DAL13 | 2 | 596 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383083 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 13 | 18 | 8 | 0 | 8 | 2 | 23 | 28 | 50 | 20 | 20 | 2 | 42 | 0 | 30 | 8 | 28 | 30 | 0 | 0.12 | 2.5455 | 0 | Bare Metal - Live | N | DAL13-101 | 2914 | 2707 | 0 | 0 | 5.621 | 0.28105 | 11.8041 |  | -5.8041 | -20.6515 | - | 0 | -
dal13.sr02.rk597 | DAL13 | 2 | 597 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383085 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 15 | 20 | 9 | 0 | 9 | 1 | 25 | 30 | 50 | 24 | 18 | 1 | 43 | 0 | 26 | 7 | 25 | 26 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-101 | 2457 | 2245 | 0 | 0 | 4.702 | 0.19592 | 8.4244 |  | -2.4244 | -12.3747 | - | 0 | -
dal13.sr02.rk598 | DAL13 | 2 | 598 | 1 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383087 | 6 | 3 | L3 | Z2-375 | 6 |  |  | 14 | 19 | 6 | 0 | 6 | 0 | 20 | 25 | 50 | 29 | 11 | 0 | 40 | 0 | 21 | 10 | 21 | 21 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-101 | 2781 | 2782 | 0 | 0 | 5.563 | 0.19183 | 7.6731 |  | -1.6731 | -8.7219 | E | 0 | -
dal13.sr02.rk599 | DAL13 | 2 | 599 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383089 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 41 | 46 | 0 | 0 | 0 | 0 | 41 | 46 | 50 | 46 | 0 | 0 | 46 | 0 | 4 | 4 | 4 | 4 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-102 | 7338 | 7328 | 0 | 0 | 14.666 | 0.31883 | 14.666 |  | -4.666 | -14.6349 | S | 0 | -
dal13.sr02.rk600 | DAL13 | 2 | 600 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383091 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 43 | 48 | 0 | 0 | 0 | 0 | 43 | 48 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.2 | 0.18182 | 0 | Compute - Live | N | DAL13-102 | 5289 | 5163 | 0 | 0 | 10.452 | 0.21775 | 10.452 |  | -0.452 | -2.0758 | - | 0 | -
dal13.sr02.rk601 | DAL13 | 2 | 601 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383093 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 41 | 46 | 0 | 0 | 0 | 0 | 41 | 46 | 50 | 46 | 0 | 0 | 46 | 0 | 4 | 4 | 4 | 4 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-102 | 6907 | 6875 | 0 | 0 | 13.782 | 0.29961 | 13.782 |  | -3.782 | -12.6231 | - | 0 | -
dal13.sr02.rk602 | DAL13 | 2 | 602 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383095 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 42 | 47 | 1 | 0 | 1 | 0 | 43 | 48 | 50 | 47 | 1 | 0 | 48 | 0 | 3 | 2 | 3 | 3 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-102 | 5133 | 5096 | 0 | 0 | 10.229 | 0.21764 | 10.4466 |  | -0.44664 | -2.0522 | - | 0 | -
dal13.sr02.rk603 | DAL13 | 2 | 603 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383097 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 34 | 39 | 4 | 0 | 4 | 0 | 38 | 43 | 50 | 39 | 4 | 0 | 43 | 0 | 11 | 7 | 11 | 11 | 0 | 0.2 | 1 | 0 | Compute - Live | N | DAL13-102 | 5555 | 5542 | 0 | 0 | 11.097 | 0.28454 | 12.2352 |  | -2.2352 | -7.8554 | - | 0 | -
dal13.sr02.rk604 | DAL13 | 2 | 604 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383099 | 5 | 3 | L3 | Z3-375 | 7 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk605 | DAL13 | 2 | 605 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383101 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 36 | 41 | 1 | 0 | 1 | 2 | 39 | 44 | 50 | 41 | 1 | 2 | 44 | 0 | 9 | 6 | 7 | 9 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-102 | 6181 | 6157 | 0 | 0 | 12.338 | 0.30093 | 13.2408 |  | -3.2408 | -10.7693 | - | 0 | -
dal13.sr02.rk606 | DAL13 | 2 | 606 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383103 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 35 | 40 | 4 | 0 | 4 | 1 | 40 | 45 | 50 | 40 | 4 | 1 | 45 | 0 | 10 | 5 | 9 | 10 | 0 | 0.2 | 0.81818 | 0 | Compute - Live | N | DAL13-102 | 5702 | 5852 | 0 | 0 | 11.554 | 0.28885 | 12.9983 |  | -2.9983 | -10.38 | - | 0 | -
dal13.sr02.rk607 | DAL13 | 2 | 607 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383105 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 34 | 39 | 3 | 0 | 3 | 0 | 37 | 42 | 50 | 39 | 3 | 0 | 42 | 0 | 11 | 8 | 11 | 11 | 0 | 0.2 | 1 | 0 | Compute - Live | N | DAL13-102 | 5837 | 5842 | 0 | 0 | 11.679 | 0.29946 | 12.5774 |  | -2.5774 | -8.6067 | - | 0 | -
dal13.sr02.rk608 | DAL13 | 2 | 608 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1383107 | 10 | 3 | L3 | Z3-375 | 7 |  |  | 38 | 43 | 1 | 0 | 1 | 1 | 40 | 45 | 50 | 44 | 1 | 1 | 46 | 0 | 6 | 4 | 5 | 6 | 0 | 0.2 | 0.45455 | 0 | Compute - Live | N | DAL13-102 | 7094 | 6359 | 0 | 0 | 13.453 | 0.30575 | 14.0645 |  | -4.0645 | -13.2935 | - | 0 | -
dal13.sr02.rk609 | DAL13 | 2 | 609 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383109 | 6 | 3 | L3 | Z3-375 | 7 |  |  | 18 | 23 | 10 | 0 | 10 | 1 | 29 | 34 | 50 | 29 | 14 | 1 | 44 | 0 | 21 | 6 | 20 | 21 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 2206 | 2264 | 0 | 0 | 4.47 | 0.15414 | 6.7821 |  | -0.78207 | -5.0738 | E | 0 | -
dal13.sr02.rk610 | DAL13 | 2 | 610 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383111 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 21 | 26 | 6 | 0 | 6 | 0 | 27 | 32 | 50 | 33 | 10 | 0 | 43 | 0 | 17 | 7 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 3167 | 3087 | 0 | 0 | 6.254 | 0.18952 | 8.1492 |  | -2.1492 | -11.3403 | S | 0 | -
dal13.sr02.rk611 | DAL13 | 2 | 611 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383113 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 21 | 26 | 5 | 0 | 5 | 1 | 27 | 32 | 50 | 35 | 8 | 1 | 44 | 0 | 15 | 6 | 14 | 15 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-102 | 3188 | 3096 | 0 | 0 | 6.284 | 0.17954 | 7.8999 |  | -1.8999 | -10.5818 | - | 0 | -
dal13.sr02.rk612 | DAL13 | 2 | 612 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383115 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 31 | 36 | 3 | 0 | 3 | 0 | 34 | 39 | 50 | 40 | 4 | 0 | 44 | 0 | 10 | 6 | 10 | 10 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-102 | 4564 | 4618 | 0 | 0 | 9.182 | 0.22955 | 10.1002 |  | -4.1002 | -17.8619 | - | 0 | -
dal13.sr02.rk613 | DAL13 | 2 | 613 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383117 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 20 | 25 | 8 | 0 | 8 | 2 | 30 | 35 | 50 | 28 | 14 | 2 | 44 | 0 | 22 | 6 | 20 | 22 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 3483 | 3247 | 0 | 0 | 6.73 | 0.24036 | 10.5757 |  | -4.5757 | -19.0371 | - | 0 | -
dal13.sr02.rk614 | DAL13 | 2 | 614 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383119 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 25 | 30 | 7 | 0 | 7 | 0 | 32 | 37 | 50 | 31 | 9 | 0 | 40 | 0 | 19 | 10 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 3209 | 3219 | 0 | 0 | 6.428 | 0.20735 | 8.2942 |  | -2.2942 | -11.0641 | - | 0 | -
dal13.sr02.rk615 | DAL13 | 2 | 615 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383121 | 5 | 3 | L3 | Z3-375 | 8 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk616 | DAL13 | 2 | 616 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383123 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 32 | 37 | 3 | 0 | 3 | 0 | 35 | 40 | 50 | 41 | 5 | 0 | 46 | 0 | 9 | 4 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-102 | 0 | 3993 | 0 | 0 | 3.993 | 0.09739 | 4.48 | 0 | 1.52 | 15.6078 | - | 0 | -
dal13.sr02.rk617 | DAL13 | 2 | 617 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383125 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 26 | 31 | 6 | 0 | 6 | 0 | 32 | 37 | 50 | 39 | 8 | 0 | 47 | 0 | 11 | 3 | 11 | 11 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 3523 | 3329 | 0 | 0 | 6.852 | 0.17569 | 8.2575 |  | -2.2575 | -12.8494 | - | 0 | -
dal13.sr02.rk618 | DAL13 | 2 | 618 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383127 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 27 | 32 | 5 | 0 | 5 | 3 | 35 | 40 | 50 | 34 | 8 | 3 | 45 | 0 | 16 | 5 | 13 | 16 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 4341 | 3839 | 0 | 0 | 8.18 | 0.24059 | 10.8265 |  | -4.8265 | -20.0611 | - | 0 | -
dal13.sr02.rk619 | DAL13 | 2 | 619 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383129 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 13 | 18 | 9 | 0 | 9 | 1 | 23 | 28 | 50 | 27 | 11 | 2 | 40 | 0 | 23 | 10 | 21 | 23 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 2642 | 2566 | 0 | 0 | 5.208 | 0.19289 | 7.7156 |  | -1.7156 | -8.894 | - | 0 | -
dal13.sr02.rk620 | DAL13 | 2 | 620 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383131 | 6 | 3 | L3 | Z3-375 | 8 |  |  | 26 | 31 | 2 | 0 | 2 | 0 | 28 | 33 | 50 | 37 | 3 | 0 | 40 | 0 | 13 | 10 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3563 | 3466 | 0 | 0 | 7.029 | 0.18997 | 7.5989 |  | -1.5989 | -8.4166 | E | 0 | -
dal13.sr02.rk621 | DAL13 | 2 | 621 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Live | 50 | 3514715 | 20 | 3 | L3 | Z1-375 | 9 | vlam - 10/28/22 - Z16 removed due to being a duplicate request. Reallocated for Dell GPU Refresh per DCL-3096 |  | 12 | 15 | 0 | 0 | 0 | 0 | 12 | 15 | 50 | 29 | 0 | 0 | 29 | 0 | 21 | 21 | 21 | 21 | 0 | 0.4 | 1.9091 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr02.rk622 | DAL13 | 2 | 622 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383135 | 0 | 3 | L3 | Z1-375 | 9 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr02.rk623 | DAL13 | 2 | 623 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Planned | 50 | 1383137 | 15 | 3 | L3 | Z1-375 | 9 | vlam - 5/12/2023 - Allocated to for NG Commercial AGG/MAGG per DCL-3096 |  | 0 | 0 | 3 | 0 | 3 | 1 | 0 | 4 | 50 | 0 | 5 | 1 | 6 | 0 | 50 | 44 | 49 | 50 | 0 | 0.3 | 4.4545 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk624 | DAL13 | 2 | 624 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Planned | 50 | 1383139 | 15 | 3 | L3 | Z1-375 | 9 | vlam - 5/12/2023 - Allocated to for NG Commercial AGG/MAGG per DCL-3096 |  | 0 | 0 | 2 | 0 | 2 | 2 | 0 | 4 | 50 | 0 | 4 | 2 | 6 | 0 | 50 | 44 | 48 | 50 | 0 | 0.3 | 4.3636 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk625 | DAL13 | 2 | 625 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Planned | 50 | 1383141 | 20 | 3 | L3 | Z1-375 | 9 | vlam - 3/26/2024 - Allocated to NG for GPU H200 - Staging per DCL-3677 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk626 | DAL13 | 2 | 626 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Planned | 50 | 1383143 | 20 | 3 | L3 | Z1-375 | 9 | vlam - 3/26/2024 - Allocated to NG for GPU H200 - Integration per DCL-3676 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk630 | DAL13 | 2 | 630 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3495909 | 20 | 3 | L3 | Z2-375 | 9 | ccoronado - Adding SL tag per Anthony Neis. Ticket:154734671 |  | 22 | 22 | 3 | 0 | 3 | 0 | 22 | 25 | 50 | 44 | 5 | 0 | 49 | 0 | 6 | 1 | 6 | 6 | 0 | 0.4 | 0.54545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr02.rk631 | DAL13 | 2 | 631 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3495911 | 20 | 3 | L3 | Z2-375 | 9 | ccoronado - Adding SL tag per Anthony Neis. Ticket:154734671 |  | 22 | 22 | 3 | 0 | 3 | 0 | 22 | 25 | 50 | 44 | 5 | 0 | 49 | 0 | 6 | 1 | 6 | 6 | 0 | 0.4 | 0.54545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr02.rk632 | DAL13 | 2 | 632 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383155 | 0 | 3 | L3 | Z2-375 | 9 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 1 | -
dal13.sr02.rk633 | DAL13 | 2 | 633 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383157 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | S | 1 | -
dal13.sr02.rk634 | DAL13 | 2 | 634 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383159 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 2 | -
dal13.sr02.rk635 | DAL13 | 2 | 635 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383161 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.12 | 2.5455 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk636 | DAL13 | 2 | 636 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383163 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk637 | DAL13 | 2 | 637 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383165 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 16 | 0 | 0 | 16 | 0 | 34 | 34 | 34 | 34 | 0 | 0.12 | 3.0909 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk638 | DAL13 | 2 | 638 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383167 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 17 | 0 | 0 | 17 | 0 | 33 | 33 | 33 | 33 | 0 | 0.12 | 3 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk639 | DAL13 | 2 | 639 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383169 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 13 | 50 | 33 | 0 | 0 | 33 | 0 | 17 | 17 | 17 | 17 | 0 | 0.12 | 1.5455 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk640 | DAL13 | 2 | 640 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383171 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.12 | 2.5455 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk641 | DAL13 | 2 | 641 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383173 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Storage - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 0 | -
dal13.sr02.rk642 | DAL13 | 2 | 642 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383175 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 1 | -
dal13.sr02.rk643 | DAL13 | 2 | 643 | 2 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1383177 | 6 | 3 | L3 | Z3-375 | 10 | dmeireles - updating status per ticket 74550221 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | Storage - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | E | 2 | -
dal13.sr02.rk644 | DAL13 | 2 | 644 | 2 | 10G | Dual Path | Unsellable | Network | Fiber | Live | 50 | 1383179 | 0 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Network - Live | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr02.rk645 | DAL13 | 2 | 645 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Planned | 50 | 1383181 | 0 | 3 | L3 | Unknown | 11 | ysilva - 5/17/2024 - Updated rack attributes of Fabric/Network-Unallocated racks to match rack's current allocation. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Unallocated - Planned | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | - | 2 | -
dal13.sr02.rk646 | DAL13 | 2 | 646 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Planned | 50 | 1383183 | 0 | 3 | L3 | Unknown | 11 | ysilva - 5/17/2024 - Updated rack attributes of Fabric/Network-Unallocated racks to match rack's current allocation. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Unallocated - Planned | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | - | 3 | -
dal13.sr02.rk647 | DAL13 | 2 | 647 | 2 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1383185 | 9.1 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.182 | 2.5455 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr02.rk648 | DAL13 | 2 | 648 | 2 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1383187 | 9.1 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.182 | 2.5455 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr02.rk649 | DAL13 | 2 | 649 | 2 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1383189 | 9.1 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.182 | 2.5455 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr02.rk650 | DAL13 | 2 | 650 | 2 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1383191 | 9.1 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 23 | 0 | 0 | 23 | 0 | 27 | 27 | 27 | 27 | 0 | 0.182 | 2.4545 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr02.rk651 | DAL13 | 2 | 651 | 2 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1382737 | 4.6 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 6 | 11 | 2 | 0 | 2 | 0 | 6 | 13 | 50 | 20 | 2 | 0 | 22 | 0 | 30 | 28 | 30 | 30 | 0 | 0.092 | 2.7273 | 0 | Fabric - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr02.rk652 | DAL13 | 2 | 652 | 2 | 10G | Dual Path | Sellable | Network | Firewall | Live | 50 | 1382739 | 6 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 0 | 12 | 0 | 12 | 5 | 0 | 17 | 50 | 0 | 12 | 5 | 17 | 0 | 50 | 33 | 45 | 50 | 0 | 0.12 | 4.0909 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 6 | 0 | - | 1 | -
dal13.sr02.rk653 | DAL13 | 2 | 653 | 2 | 10G | Dual Path | Unsellable | Fabric | Server | Live | 50 | 1382741 | 4.6 | 3 | L3 | Unknown | 11 | ysilva - 5/17/2024 - Updated rack attributes of Fabric/Network-Unallocated racks to match rack's current allocation. |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 50 | 2 | 0 | 0 | 2 | 0 | 48 | 48 | 48 | 48 | 0 | 0.092 | 4.3636 | 0 | Fabric - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.6 | 0 | - | 0 | -
dal13.sr02.rk654 | DAL13 | 2 | 654 | 2 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1382743 | 9.1 | 3 | L3 | Unknown | 11 | dmeireles - updating status per ticket 74550221 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 12 | 0 | 0 | 12 | 0 | 38 | 38 | 38 | 38 | 0 | 0.182 | 3.4545 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.1 | 0 | - | 0 | -
dal13.sr02.rk655 | DAL13 | 2 | 655 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Planned | 50 | 1382745 | 0 | 3 | L3 | Unknown | 11 | ysilva - 5/17/2024 - Updated rack attributes of Fabric/Network-Unallocated racks to match rack's current allocation. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Unallocated - Planned | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | E | 1 | -
dal13.sr02.rk656 | DAL13 | 2 | 656 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Live | 50 | 3514831 | 20 | 3 | L3 | Z4-375 | 12 | vlam - 10/28/22 - Z16 removed due to being a duplicate request. Reallocated for Dell GPU Refresh per DCL-3096 |  | 12 | 15 | 0 | 0 | 0 | 0 | 12 | 15 | 50 | 29 | 0 | 0 | 29 | 0 | 21 | 21 | 21 | 21 | 0 | 0.4 | 1.9091 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr02.rk657 | DAL13 | 2 | 657 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382749 | 0 | 3 | L3 | Z4-375 | 12 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr02.rk658 | DAL13 | 2 | 658 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 3549027 | 20 | 3 | L3 | Z4-375 | 12 | vlam - 5/10/2024 - Allocated to QZ2 per DCL-3096. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk659 | DAL13 | 2 | 659 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1382753 | 20 | 3 | L3 | Z4-375 | 12 | vlam - 3/25/2024 - Allocated to NG for NG2 - BAU per DCL-3671. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk660 | DAL13 | 2 | 660 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Planned | 50 | 1382755 | 20 | 3 | L3 | Z4-375 | 12 | vlam - 7/28/2023 - DAL13 QZ2 Dev GPU Rack 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk661 | DAL13 | 2 | 661 | G1 | 10G | Dual Path | Sellable | Gen2 | GPU | Planned | 50 | 1382757 | 20 | 3 | L3 | Z4-375 | 12 | vlam - 7/28/2023 - DAL13 QZ1 Staging GPU Rack 1 |  | 0 | 0 | 4 | 0 | 4 | 0 | 0 | 4 | 50 | 0 | 6 | 0 | 6 | 0 | 50 | 44 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk662 | DAL13 | 2 | 662 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382759 | 0 | 3 | L3 | Z4-375 | 12 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr02.rk663 | DAL13 | 2 | 663 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382761 | 0 | 3 | L3 | Z4-375 | 12 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr02.rk664 | DAL13 | 2 | 664 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382763 | 0 | 3 | L3 | Z4-375 | 12 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr02.rk665 | DAL13 | 2 | 665 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382765 | 0 | 3 | L3 | Z4-375 | 12 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr02.rk666 | DAL13 | 2 | 666 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382767 | 0 | 3 | L3 | Z4-375 | 12 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 5 | -
dal13.sr02.rk667 | DAL13 | 2 | 667 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382769 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 40 | 45 | 0 | 0 | 0 | 0 | 40 | 45 | 50 | 45 | 0 | 0 | 45 | 0 | 5 | 5 | 5 | 5 | 0 | 0.2 | 0.45455 | 0 | Compute - Live | N | DAL13-102 | 5827 | 5017 | 0 | 0 | 10.844 | 0.24098 | 10.844 |  | -0.844 | -3.5024 | S | 0 | -
dal13.sr02.rk668 | DAL13 | 2 | 668 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382771 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 39 | 44 | 1 | 0 | 1 | 0 | 40 | 45 | 50 | 44 | 1 | 0 | 45 | 0 | 6 | 5 | 6 | 6 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-102 | 5216 | 5153 | 0 | 0 | 10.369 | 0.23566 | 10.6047 |  | -0.60466 | -2.5658 | - | 0 | -
dal13.sr02.rk669 | DAL13 | 2 | 669 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382773 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 35 | 40 | 1 | 0 | 1 | 1 | 37 | 42 | 50 | 40 | 1 | 1 | 42 | 0 | 10 | 8 | 9 | 10 | 0 | 0.2 | 0.81818 | 0 | Compute - Live | N | DAL13-102 | 4701 | 5192 | 0 | 0 | 9.893 | 0.24733 | 10.3877 |  | -0.38765 | -1.5674 | - | 0 | -
dal13.sr02.rk670 | DAL13 | 2 | 670 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382775 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 37 | 42 | 0 | 0 | 0 | 0 | 37 | 42 | 50 | 42 | 0 | 0 | 42 | 0 | 8 | 8 | 8 | 8 | 0 | 0.2 | 0.72727 | 0 | Compute - Live | N | DAL13-102 | 4728 | 5895 | 0 | 0 | 10.623 | 0.25293 | 10.623 |  | -0.623 | -2.4631 | - | 0 | -
dal13.sr02.rk671 | DAL13 | 2 | 671 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382777 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 37 | 42 | 0 | 0 | 0 | 1 | 38 | 43 | 50 | 42 | 0 | 1 | 43 | 0 | 8 | 7 | 7 | 8 | 0 | 0.2 | 0.63636 | 0 | Compute - Live | N | DAL13-102 | 5563 | 0 | 0 | 0 | 5.563 | 0.13245 | 5.6955 | 0 | 4.3045 | 32.4988 | - | 0 | -
dal13.sr02.rk672 | DAL13 | 2 | 672 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1382779 | 5 | 3 | L3 | Z4-375 | 13 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk673 | DAL13 | 2 | 673 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382781 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 39 | 44 | 2 | 0 | 2 | 1 | 42 | 47 | 50 | 44 | 2 | 1 | 47 | 0 | 6 | 3 | 5 | 6 | 0 | 0.2 | 0.45455 | 0 | Compute - Live | N | DAL13-102 | 5338 | 5349 | 0 | 0 | 10.687 | 0.24289 | 11.4157 |  | -1.4157 | -5.8285 | - | 0 | -
dal13.sr02.rk674 | DAL13 | 2 | 674 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382783 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 33 | 38 | 4 | 0 | 4 | 2 | 39 | 44 | 50 | 38 | 4 | 2 | 44 | 0 | 12 | 6 | 10 | 12 | 0 | 0.2 | 0.90909 | 0 | Compute - Live | N | DAL13-102 | 5201 | 4991 | 0 | 0 | 10.192 | 0.26821 | 11.8013 |  | -1.8013 | -6.7159 | - | 0 | -
dal13.sr02.rk675 | DAL13 | 2 | 675 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382785 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 38 | 43 | 0 | 0 | 0 | 1 | 39 | 44 | 50 | 43 | 0 | 1 | 44 | 0 | 7 | 6 | 6 | 7 | 0 | 0.2 | 0.54545 | 0 | Compute - Live | N | DAL13-102 | 5458 | 5421 | 0 | 0 | 10.879 | 0.253 | 11.132 |  | -1.132 | -4.4743 | - | 0 | -
dal13.sr02.rk676 | DAL13 | 2 | 676 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382787 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 41 | 46 | 1 | 0 | 1 | 0 | 42 | 47 | 50 | 46 | 1 | 0 | 47 | 0 | 4 | 3 | 4 | 4 | 0 | 0.2 | 0.36364 | 0 | Compute - Live | N | DAL13-102 | 0 | 6239 | 0 | 0 | 6.239 | 0.13563 | 6.3746 | ERROR | 3.6254 | 26.7298 | - | 0 | -
dal13.sr02.rk677 | DAL13 | 2 | 677 | 2 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1382789 | 10 | 3 | L3 | Z4-375 | 13 |  |  | 42 | 47 | 0 | 0 | 0 | 0 | 42 | 47 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.2 | 0.27273 | 0 | Compute - Live | N | DAL13-102 | 6310 | 6350 | 0 | 0 | 12.66 | 0.26936 | 12.66 |  | -2.66 | -9.8752 | E | 0 | -
dal13.sr02.rk678 | DAL13 | 2 | 678 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382791 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 24 | 29 | 0 | 0 | 0 | 2 | 26 | 31 | 50 | 38 | 0 | 2 | 40 | 0 | 12 | 10 | 10 | 12 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-102 | 3001 | 2854 | 0 | 0 | 5.855 | 0.15408 | 6.1632 |  | -0.16316 | -1.0589 | S | 0 | -
dal13.sr02.rk679 | DAL13 | 2 | 679 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383193 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 18 | 23 | 6 | 0 | 6 | 1 | 25 | 30 | 50 | 31 | 8 | 1 | 40 | 0 | 19 | 10 | 18 | 19 | 0 | 0.12 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-102 | 2174 | 2267 | 0 | 0 | 4.441 | 0.14326 | 5.7303 |  | 0.26968 | 1.8825 | - | 0 | -
dal13.sr02.rk680 | DAL13 | 2 | 680 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383195 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 18 | 23 | 7 | 0 | 7 | 0 | 25 | 30 | 50 | 30 | 11 | 0 | 41 | 0 | 20 | 9 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 2529 | 2198 | 0 | 0 | 4.727 | 0.15757 | 6.4602 |  | -0.46023 | -2.9209 | - | 0 | -
dal13.sr02.rk681 | DAL13 | 2 | 681 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383197 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 18 | 23 | 5 | 0 | 5 | 2 | 25 | 30 | 50 | 27 | 6 | 2 | 35 | 0 | 23 | 15 | 21 | 23 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 2181 | 2040 | 0 | 0 | 4.221 | 0.15633 | 5.4717 |  | 0.52833 | 3.3795 | - | 0 | -
dal13.sr02.rk682 | DAL13 | 2 | 682 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383199 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 20 | 25 | 8 | 0 | 8 | 0 | 28 | 33 | 50 | 28 | 12 | 0 | 40 | 0 | 22 | 10 | 22 | 22 | 0 | 0.12 | 2 | 0 | Bare Metal - Live | N | DAL13-102 | 2724 | 2646 | 0 | 0 | 5.37 | 0.19179 | 7.6714 |  | -1.6714 | -8.7151 | - | 0 | -
dal13.sr02.rk683 | DAL13 | 2 | 683 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383201 | 5 | 3 | L3 | Z4-375 | 14 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk684 | DAL13 | 2 | 684 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383203 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 22 | 27 | 10 | 0 | 10 | 1 | 33 | 38 | 50 | 34 | 11 | 1 | 46 | 0 | 16 | 4 | 15 | 16 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 2800 | 2934 | 0 | 0 | 5.734 | 0.16865 | 7.7578 |  | -1.7578 | -10.4227 | - | 0 | -
dal13.sr02.rk685 | DAL13 | 2 | 685 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383205 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 15 | 20 | 9 | 0 | 9 | 0 | 24 | 29 | 50 | 31 | 14 | 0 | 45 | 0 | 19 | 5 | 19 | 19 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 2402 | 2202 | 0 | 0 | 4.604 | 0.14852 | 6.6832 |  | -0.68323 | -4.6003 | - | 0 | -
dal13.sr02.rk686 | DAL13 | 2 | 686 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383207 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 20 | 25 | 12 | 0 | 12 | 0 | 32 | 37 | 50 | 30 | 16 | 0 | 46 | 0 | 20 | 4 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 2777 | 2493 | 0 | 0 | 5.27 | 0.17567 | 8.0807 |  | -2.0807 | -11.8444 | - | 0 | -
dal13.sr02.rk687 | DAL13 | 2 | 687 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383209 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 21 | 26 | 9 | 0 | 9 | 0 | 30 | 35 | 50 | 30 | 13 | 0 | 43 | 0 | 20 | 7 | 20 | 20 | 0 | 0.12 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-102 | 2553 | 2352 | 0 | 0 | 4.905 | 0.1635 | 7.0305 |  | -1.0305 | -6.3028 | - | 0 | -
dal13.sr02.rk688 | DAL13 | 2 | 688 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383211 | 6 | 3 | L3 | Z4-375 | 14 |  |  | 22 | 27 | 4 | 0 | 4 | 0 | 26 | 31 | 50 | 37 | 5 | 0 | 42 | 0 | 13 | 8 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3430 | 3091 | 0 | 0 | 6.521 | 0.17624 | 7.4022 |  | -1.4022 | -7.9561 | E | 0 | -
dal13.sr02.rk689 | DAL13 | 2 | 689 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383213 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 21 | 26 | 3 | 0 | 3 | 2 | 26 | 31 | 50 | 42 | 4 | 2 | 48 | 0 | 8 | 2 | 6 | 8 | 0 | 0.12 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-102 | 3995 | 4280 | 0 | 0 | 8.275 | 0.19702 | 9.4571 |  | -3.4571 | -17.5468 | S | 0 | -
dal13.sr02.rk690 | DAL13 | 2 | 690 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383215 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 15 | 20 | 6 | 0 | 6 | 1 | 22 | 27 | 50 | 31 | 11 | 4 | 46 | 0 | 19 | 4 | 15 | 19 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 2747 | 2579 | 0 | 0 | 5.326 | 0.17181 | 7.9031 |  | -1.9031 | -11.077 | - | 0 | -
dal13.sr02.rk691 | DAL13 | 2 | 691 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383217 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 22 | 27 | 4 | 0 | 4 | 1 | 27 | 32 | 50 | 37 | 7 | 2 | 46 | 0 | 13 | 4 | 11 | 13 | 0 | 0.12 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 3207 | 3264 | 0 | 0 | 6.471 | 0.17489 | 8.045 |  | -2.045 | -11.6931 | - | 0 | -
dal13.sr02.rk692 | DAL13 | 2 | 692 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383219 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 30 | 35 | 3 | 0 | 3 | 0 | 33 | 38 | 50 | 41 | 4 | 0 | 45 | 0 | 9 | 5 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-102 | 3198 | 3639 | 0 | 0 | 6.837 | 0.16676 | 7.504 |  | -1.504 | -9.0193 | - | 0 | -
dal13.sr02.rk693 | DAL13 | 2 | 693 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383221 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 16 | 21 | 5 | 0 | 5 | 1 | 22 | 27 | 50 | 32 | 8 | 2 | 42 | 0 | 18 | 8 | 16 | 18 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 2683 | 2876 | 0 | 0 | 5.559 | 0.17372 | 7.2962 |  | -1.2962 | -7.4614 | - | 0 | -
dal13.sr02.rk694 | DAL13 | 2 | 694 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1383223 | 5 | 3 | L3 | Z5-375 | 15 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk695 | DAL13 | 2 | 695 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383225 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 25 | 30 | 9 | 0 | 9 | 1 | 35 | 40 | 50 | 34 | 12 | 1 | 47 | 0 | 16 | 3 | 15 | 16 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 3552 | 4055 | 0 | 0 | 7.607 | 0.22374 | 10.5156 |  | -4.5156 | -20.1826 | - | 0 | -
dal13.sr02.rk696 | DAL13 | 2 | 696 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383227 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 41 | 46 | 0 | 0 | 0 | 0 | 41 | 46 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.12 | 0.27273 | 0 | Bare Metal - Live | N | DAL13-102 | 2863 | 2821 | 0 | 0 | 5.684 | 0.12094 | 5.684 |  | 0.316 | 2.6129 | - | 0 | -
dal13.sr02.rk697 | DAL13 | 2 | 697 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383229 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 26 | 31 | 6 | 0 | 6 | 2 | 34 | 39 | 50 | 34 | 6 | 2 | 42 | 0 | 16 | 8 | 14 | 16 | 0 | 0.12 | 1.2727 | 0 | Bare Metal - Live | N | DAL13-102 | 3663 | 3448 | 0 | 0 | 7.111 | 0.20915 | 8.7842 |  | -2.7842 | -13.3121 | - | 0 | -
dal13.sr02.rk698 | DAL13 | 2 | 698 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383231 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 29 | 34 | 7 | 0 | 7 | 0 | 36 | 41 | 50 | 37 | 7 | 0 | 44 | 0 | 13 | 6 | 13 | 13 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 2978 | 2947 | 0 | 0 | 5.925 | 0.16014 | 7.0459 |  | -1.0459 | -6.5316 | - | 0 | -
dal13.sr02.rk699 | DAL13 | 2 | 699 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383233 | 6 | 3 | L3 | Z5-375 | 15 |  |  | 30 | 35 | 9 | 0 | 9 | 0 | 39 | 44 | 50 | 35 | 12 | 0 | 47 | 0 | 15 | 3 | 15 | 15 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 3722 | 4408 | 0 | 0 | 8.13 | 0.23229 | 10.9174 |  | -4.9174 | -21.1697 | E | 0 | -
dal13.sr02.rk700 | DAL13 | 2 | 700 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1383235 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 39 | 44 | 1 | 0 | 1 | 0 | 40 | 45 | 50 | 46 | 1 | 0 | 47 | 0 | 4 | 3 | 4 | 4 | 0 | 0.12 | 0.36364 | 0 | Bare Metal - Live | N | DAL13-102 | 6969 | 6945 | 0 | 0 | 13.914 | 0.30248 | 14.2165 |  | -8.2165 | -27.1639 | S | 0 | -
dal13.sr02.rk701 | DAL13 | 2 | 701 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382929 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 43 | 48 | 0 | 0 | 0 | 0 | 43 | 48 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.12 | 0.18182 | 0 | Bare Metal - Live | N | DAL13-102 | 7486 | 7226 | 0 | 0 | 14.712 | 0.3065 | 14.712 |  | -8.712 | -28.4241 | - | 0 | -
dal13.sr02.rk702 | DAL13 | 2 | 702 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382931 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 35 | 40 | 5 | 0 | 5 | 0 | 40 | 45 | 50 | 40 | 7 | 0 | 47 | 0 | 10 | 3 | 10 | 10 | 0 | 0.12 | 0.90909 | 0 | Bare Metal - Live | N | DAL13-102 | 5947 | 5991 | 0 | 0 | 11.938 | 0.29845 | 14.0271 |  | -8.0271 | -26.8961 | - | 0 | -
dal13.sr02.rk703 | DAL13 | 2 | 703 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382933 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 29 | 34 | 7 | 0 | 7 | 0 | 36 | 41 | 50 | 35 | 10 | 0 | 45 | 0 | 15 | 5 | 15 | 15 | 0 | 0.12 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 3874 | 3900 | 0 | 0 | 7.774 | 0.22211 | 9.9951 |  | -3.9951 | -17.9869 | - | 0 | -
dal13.sr02.rk704 | DAL13 | 2 | 704 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382935 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 40 | 45 | 1 | 0 | 1 | 0 | 41 | 46 | 50 | 45 | 1 | 0 | 46 | 0 | 5 | 4 | 5 | 5 | 0 | 0.12 | 0.45455 | 0 | Bare Metal - Live | N | DAL13-102 | 4983 | 5020 | 0 | 0 | 10.003 | 0.22229 | 10.2253 |  | -4.2253 | -19.0081 | - | 0 | -
dal13.sr02.rk705 | DAL13 | 2 | 705 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1382937 | 5 | 3 | L3 | Z5-375 | 16 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk706 | DAL13 | 2 | 706 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382939 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 28 | 33 | 4 | 0 | 4 | 2 | 34 | 39 | 50 | 35 | 7 | 2 | 44 | 0 | 15 | 6 | 13 | 15 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 3594 | 3279 | 0 | 0 | 6.873 | 0.19637 | 8.6403 |  | -2.6403 | -13.4457 | - | 0 | -
dal13.sr02.rk707 | DAL13 | 2 | 707 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382941 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 36 | 41 | 2 | 0 | 2 | 0 | 38 | 43 | 50 | 41 | 3 | 0 | 44 | 0 | 9 | 6 | 9 | 9 | 0 | 0.12 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-102 | 4271 | 4304 | 0 | 0 | 8.575 | 0.20915 | 9.2024 |  | -3.2024 | -15.312 | - | 0 | -
dal13.sr02.rk708 | DAL13 | 2 | 708 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382943 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 19 | 24 | 7 | 0 | 7 | 1 | 27 | 32 | 50 | 31 | 12 | 2 | 45 | 0 | 19 | 5 | 17 | 19 | 0 | 0.12 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 2975 | 2746 | 0 | 0 | 5.721 | 0.18455 | 8.3047 |  | -2.3047 | -12.4882 | - | 0 | -
dal13.sr02.rk709 | DAL13 | 2 | 709 | 2 | 10G | Dual Path | Sellable | Network | Ded. Firewall | Live | 50 | 1382945 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 50 | 24 | 0 | 0 | 24 | 0 | 26 | 26 | 26 | 26 | 0 | 0.12 | 2.3636 | 0 | Network - Live | N | DAL13-102 | 2106 | 0 | 0 | 0 | 2.106 | 0.08775 | 2.106 | ERROR | 3.894 | 44.3761 | - | 0 | -
dal13.sr02.rk710 | DAL13 | 2 | 710 | 2 | 10G | Dual Path | Sellable | Bare Metal | COD | Live | 50 | 1382947 | 6 | 3 | L3 | Z5-375 | 16 |  |  | 2 | 10 | 2 | 0 | 2 | 1 | 2 | 13 | 50 | 12 | 2 | 1 | 15 | 0 | 38 | 35 | 37 | 38 | 0 | 0.12 | 3.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 688 | 526 | 0 | 0 | 1.214 | 0.10117 | 1.5175 |  | 4.4825 | 44.3081 | E | 0 | -
dal13.sr02.rk711 | DAL13 | 2 | 711 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1382949 | 0 | 3 | L3 | Z6-375 | 17 | vlam - 2/8/2024 - No longer needed for NGDC Z Mainframe. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr02.rk712 | DAL13 | 2 | 712 | G1 | 10G | Dual Path | Sellable | NGDC | Bare Metal | Planned | 50 | 1382951 | 20 | 3 | L3 | Z6-375 | 17 | vlam - 2/8/2024 - Allocated to NGDC Staging BM per DCL-3372 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk713 | DAL13 | 2 | 713 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382953 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk714 | DAL13 | 2 | 714 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382955 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 6 | 0 | 6 | 6 | 4 | 12 | 50 | 0 | 12 | 6 | 18 | 0 | 50 | 32 | 44 | 50 | 0 | 0.3 | 4 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk715 | DAL13 | 2 | 715 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382957 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk716 | DAL13 | 2 | 716 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382959 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 4 | 0 | 4 | 0 | 0 | 4 | 50 | 0 | 12 | 0 | 12 | 0 | 50 | 38 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk717 | DAL13 | 2 | 717 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Live | 50 | 1382961 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.3 | 4.4545 | 0 | NGDC - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr02.rk718 | DAL13 | 2 | 718 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382963 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 50 | 0 | 26 | 0 | 26 | 0 | 50 | 24 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk719 | DAL13 | 2 | 719 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382965 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 50 | 0 | 26 | 0 | 26 | 0 | 50 | 24 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk720 | DAL13 | 2 | 720 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1382967 | 15 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 1 | 0 | 1 | 3 | 0 | 4 | 50 | 0 | 7 | 9 | 16 | 0 | 50 | 34 | 41 | 50 | 0 | 0.3 | 3.7273 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk721 | DAL13 | 2 | 721 | 2 | 10G | Dual Path | Unsellable | Network | Fiber | Planned | 50 | 1382969 | 0 | 3 | L3 | Z6-375 | 17 | vlam - 10/3/2023 - Allocated to NG per DCL-3371. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Network - Planned | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | E | 1 | -
dal13.sr02.rk722 | DAL13 | 2 | 722 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382971 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 10 | 15 | 8 | 0 | 8 | 2 | 20 | 25 | 50 | 18 | 16 | 6 | 40 | 0 | 32 | 10 | 26 | 32 | 0 | 0.12 | 2.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 2846 | 1971 | 0 | 0 | 4.817 | 0.26761 | 10.7044 |  | -4.7044 | -17.5794 | S | 0 | -
dal13.sr02.rk723 | DAL13 | 2 | 723 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382973 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 17 | 22 | 7 | 0 | 7 | 1 | 25 | 30 | 50 | 27 | 14 | 4 | 45 | 0 | 23 | 5 | 19 | 23 | 0 | 0.12 | 1.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 3474 | 3148 | 0 | 0 | 6.622 | 0.24526 | 11.0367 |  | -5.0367 | -20.5361 | - | 0 | -
dal13.sr02.rk724 | DAL13 | 2 | 724 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382975 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 21 | 26 | 7 | 0 | 7 | 0 | 28 | 33 | 50 | 29 | 7 | 0 | 36 | 0 | 21 | 14 | 21 | 21 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 1919 | 2380 | 0 | 0 | 4.299 | 0.14824 | 5.3367 |  | 0.66331 | 4.4745 | - | 0 | -
dal13.sr02.rk725 | DAL13 | 2 | 725 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382977 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 22 | 27 | 2 | 0 | 2 | 1 | 25 | 30 | 50 | 28 | 2 | 1 | 31 | 0 | 22 | 19 | 21 | 22 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 2507 | 2434 | 0 | 0 | 4.941 | 0.17646 | 5.4704 |  | 0.52961 | 3.0012 | - | 0 | -
dal13.sr02.rk726 | DAL13 | 2 | 726 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382979 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 12 | 17 | 4 | 0 | 4 | 1 | 17 | 22 | 50 | 18 | 12 | 2 | 32 | 0 | 32 | 18 | 30 | 32 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-102 | 1715 | 1651 | 0 | 0 | 3.366 | 0.187 | 5.984 |  | 0.016 | 0.085561 | - | 0 | -
dal13.sr02.rk727 | DAL13 | 2 | 727 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1382981 | 5 | 3 | L3 | Z5-375 | 18 |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr02.rk728 | DAL13 | 2 | 728 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382983 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 17 | 22 | 11 | 0 | 11 | 1 | 29 | 34 | 50 | 23 | 19 | 2 | 44 | 0 | 27 | 6 | 25 | 27 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-102 | 2681 | 2602 | 0 | 0 | 5.283 | 0.2297 | 10.1066 |  | -4.1066 | -17.8785 | - | 0 | -
dal13.sr02.rk729 | DAL13 | 2 | 729 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382985 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 16 | 21 | 8 | 0 | 8 | 4 | 28 | 33 | 50 | 24 | 13 | 5 | 42 | 0 | 26 | 8 | 21 | 26 | 0 | 0.12 | 1.9091 | 0 | Bare Metal - Live | N | DAL13-102 | 1634 | 951 | 0 | 0 | 2.585 | 0.10771 | 4.5237 |  | 1.4763 | 13.706 | - | 0 | -
dal13.sr02.rk730 | DAL13 | 2 | 730 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382987 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 30 | 35 | 8 | 0 | 8 | 1 | 39 | 44 | 50 | 36 | 8 | 1 | 45 | 0 | 14 | 5 | 13 | 14 | 0 | 0.12 | 1.1818 | 0 | Bare Metal - Live | N | DAL13-102 | 4490 | 4586 | 0 | 0 | 9.076 | 0.25211 | 11.345 |  | -5.345 | -21.201 | - | 0 | -
dal13.sr02.rk731 | DAL13 | 2 | 731 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382989 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 31 | 36 | 2 | 0 | 2 | 1 | 34 | 39 | 50 | 42 | 3 | 2 | 47 | 0 | 8 | 3 | 6 | 8 | 0 | 0.12 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-102 | 5154 | 5128 | 0 | 0 | 10.282 | 0.24481 | 11.506 |  | -5.506 | -22.4911 | - | 0 | -
dal13.sr02.rk732 | DAL13 | 2 | 732 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1382991 | 6 | 3 | L3 | Z5-375 | 18 |  |  | 43 | 48 | 0 | 0 | 0 | 0 | 43 | 48 | 50 | 48 | 0 | 0 | 48 | 0 | 2 | 2 | 2 | 2 | 0 | 0.12 | 0.18182 | 0 | Bare Metal - Live | N | DAL13-102 | 6411 | 6430 | 0 | 0 | 12.841 | 0.26752 | 12.841 |  | -6.841 | -25.5718 | E | 0 | -
dal13.sr02.rk733 | DAL13 | 2 | 733 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 1383293 | 15 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3373 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | S | 0 | -
dal13.sr02.rk734 | DAL13 | 2 | 734 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 1383295 | 15 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3373 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk735 | DAL13 | 2 | 735 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 1383297 | 15 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3373 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk736 | DAL13 | 2 | 736 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 1383299 | 15 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3373 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr02.rk737 | DAL13 | 2 | 737 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383301 | 0 | 3 | L3 | Z6-375 | 19 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr02.rk738 | DAL13 | 2 | 738 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383303 | 0 | 3 | L3 | Z6-375 | 19 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr02.rk739 | DAL13 | 2 | 739 | G1 | 10G | Dual Path | Sellable | NGDC | File/Block | Planned | 50 | 1383305 | 6 | 3 | L3 | Z6-375 | 19 | vlam - 8/7/2023 - Allocated to FedRAMP Staging - File/Block per DCL-3096 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | - | 0 | -
dal13.sr02.rk740 | DAL13 | 2 | 740 | G1 | 10G | Dual Path | Sellable | NGDC | File/Block | Planned | 50 | 1383307 | 6 | 3 | L3 | Z6-375 | 19 | vlam - 8/7/2023 - Allocated to FedRAMP Staging - File/Block per DCL-3096 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | - | 0 | -
dal13.sr02.rk741 | DAL13 | 2 | 741 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 1383309 | 20 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3374 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk742 | DAL13 | 2 | 742 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 1383311 | 20 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3374 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk743 | DAL13 | 2 | 743 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 1383313 | 20 | 3 | L3 | Z6-375 | 19 | vlam - 10/3/2023 - Allocated to NG per DCL-3374 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | E | 0 | -
dal13.sr02.rk744 | DAL13 | 2 | 744 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383315 | 0 | 3 | L3 | Z6-375 | 20 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr02.rk745 | DAL13 | 2 | 745 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383317 | 0 | 3 | L3 | Z6-375 | 20 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr02.rk746 | DAL13 | 2 | 746 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383319 | 0 | 3 | L3 | Z6-375 | 20 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr02.rk747 | DAL13 | 2 | 747 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383321 | 0 | 3 | L3 | Z6-375 | 20 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr02.rk748 | DAL13 | 2 | 748 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383323 | 0 | 3 | L3 | Z6-375 | 20 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr02.rk749 | DAL13 | 2 | 749 | 2 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1383325 | 0 | 3 | L3 | Z6-375 | 20 | vlam - 10/27/2022 - Set status to Decom to prepare for customer migrations. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr02.rk750 | DAL13 | 2 | 750 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1383327 | 20 | 3 | L3 | Z6-375 | 20 | vlam - 10/3/2023 - Allocated to NG per DCL-3370. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk751 | DAL13 | 2 | 751 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1382845 | 20 | 3 | L3 | Z6-375 | 20 | vlam - 10/3/2023 - Allocated to NG per DCL-3370. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk752 | DAL13 | 2 | 752 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1382847 | 20 | 3 | L3 | Z6-375 | 20 | vlam - 2/6/2024 - L4/L40 allocation moved to SR01. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk753 | DAL13 | 2 | 753 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1382849 | 20 | 3 | L3 | Z6-375 | 20 | vlam - 2/6/2024 - L4/L40 allocation moved to SR01. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr02.rk754 | DAL13 | 2 | 754 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1382851 | 20 | 3 | L3 | Z6-375 | 20 | vlam - 3/25/2024 - Allocated to NG for NG2 - BAU per DCL-3671. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | E | 0 | -
dal13.sr03.rk01 | DAL13 | 3 | 1 | 2 | 10G | Dual Path | Sellable | Bare Metal | VDC | Power Limit | 50 | 1944760 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 7 | 12 | 9 | 0 | 9 | 2 | 18 | 23 | 50 | 19 | 15 | 3 | 37 | 0 | 0 | 13 | 28 | 31 | 31 | 0.1 | 2.5455 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 3410 | 3328 | 0 | 0 | 6.738 | 0.35463 | 13.1214 |  | -8.1214 | -22.9009 | S | 0 | -
dal13.sr03.rk02 | DAL13 | 3 | 2 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944762 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 15 | 20 | 3 | 0 | 3 | 0 | 18 | 23 | 50 | 26 | 4 | 0 | 30 | 0 | 0 | 20 | 24 | 24 | 24 | 0.1 | 2.1818 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2210 | 2178 | 0 | 0 | 4.388 | 0.16877 | 5.0631 |  | -0.063077 | -0.37375 | - | 0 | -
dal13.sr03.rk03 | DAL13 | 3 | 3 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944764 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 15 | 20 | 3 | 0 | 3 | 2 | 20 | 25 | 50 | 21 | 7 | 3 | 31 | 0 | 0 | 19 | 26 | 29 | 29 | 0.1 | 2.3636 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1754 | 1724 | 0 | 0 | 3.478 | 0.16562 | 5.1342 |  | -0.13419 | -0.81024 | - | 0 | -
dal13.sr03.rk04 | DAL13 | 3 | 4 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944766 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 10 | 15 | 3 | 0 | 3 | 1 | 14 | 19 | 50 | 18 | 5 | 2 | 25 | 0 | 0 | 25 | 30 | 32 | 32 | 0.1 | 2.7273 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1281 | 1120 | 0 | 0 | 2.401 | 0.13339 | 3.3347 |  | 1.6653 | 12.4844 | - | 0 | -
dal13.sr03.rk05 | DAL13 | 3 | 5 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944768 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 9 | 14 | 1 | 0 | 1 | 3 | 13 | 18 | 50 | 16 | 2 | 5 | 23 | 0 | 0 | 27 | 29 | 34 | 34 | 0.1 | 2.6364 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1367 | 1342 | 0 | 0 | 2.709 | 0.16931 | 3.8942 |  | 1.1058 | 6.5312 | - | 0 | -
dal13.sr03.rk06 | DAL13 | 3 | 6 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Power Limit | 50 | 1944770 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 0 | 46 | 46 | 46 | 46 | 0.1 | 4.1818 | 0 | Network - Power Limit | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk07 | DAL13 | 3 | 7 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944772 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 10 | 15 | 4 | 0 | 4 | 2 | 16 | 21 | 50 | 18 | 7 | 4 | 29 | 0 | 0 | 21 | 28 | 32 | 32 | 0.1 | 2.5455 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1279 | 1317 | 0 | 0 | 2.596 | 0.14422 | 4.1824 |  | 0.81756 | 5.6687 | - | 0 | -
dal13.sr03.rk08 | DAL13 | 3 | 8 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944774 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 11 | 16 | 1 | 0 | 1 | 0 | 12 | 17 | 50 | 18 | 2 | 0 | 20 | 0 | 0 | 30 | 32 | 32 | 32 | 0.1 | 2.9091 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1748 | 1389 | 0 | 0 | 3.137 | 0.17428 | 3.4856 |  | 1.5144 | 8.6898 | - | 0 | -
dal13.sr03.rk09 | DAL13 | 3 | 9 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944776 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 17 | 22 | 0 | 0 | 0 | 0 | 17 | 22 | 50 | 23 | 0 | 0 | 23 | 0 | 0 | 27 | 27 | 27 | 27 | 0.1 | 2.4545 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 3186 | 2709 | 0 | 0 | 5.895 | 0.2563 | 5.895 |  | -0.895 | -3.4919 | - | 0 | -
dal13.sr03.rk10 | DAL13 | 3 | 10 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944778 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 29 | 34 | 0 | 0 | 0 | 0 | 29 | 34 | 50 | 34 | 0 | 0 | 34 | 0 | 0 | 16 | 16 | 16 | 16 | 0.1 | 1.4545 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 5158 | 5155 | 0 | 0 | 10.313 | 0.30332 | 10.313 |  | -5.313 | -17.516 | - | 0 | -
dal13.sr03.rk11 | DAL13 | 3 | 11 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944780 | 5 | 4 | L4 | Z6-375 | 1 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 24 | 29 | 0 | 0 | 0 | 0 | 24 | 29 | 50 | 29 | 0 | 0 | 29 | 0 | 0 | 21 | 21 | 21 | 21 | 0.1 | 1.9091 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 4377 | 4341 | 0 | 0 | 8.718 | 0.30062 | 8.718 |  | -3.718 | -12.3677 | E | 0 | -
dal13.sr03.rk12 | DAL13 | 3 | 12 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944782 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 15 | 20 | 2 | 0 | 2 | 0 | 17 | 22 | 50 | 26 | 3 | 0 | 29 | 0 | 0 | 21 | 24 | 24 | 24 | 0.1 | 2.1818 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1763 | 1803 | 0 | 0 | 3.566 | 0.13715 | 3.9775 |  | 1.0225 | 7.4554 | S | 0 | -
dal13.sr03.rk13 | DAL13 | 3 | 13 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944784 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 17 | 22 | 4 | 0 | 4 | 0 | 21 | 26 | 50 | 26 | 8 | 0 | 34 | 0 | 0 | 16 | 24 | 24 | 24 | 0.1 | 2.1818 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2507 | 2387 | 0 | 0 | 4.894 | 0.18823 | 6.3998 |  | -1.3998 | -7.4369 | - | 0 | -
dal13.sr03.rk14 | DAL13 | 3 | 14 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944786 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 19 | 24 | 5 | 0 | 5 | 0 | 24 | 29 | 50 | 25 | 12 | 0 | 37 | 0 | 0 | 13 | 25 | 25 | 25 | 0.1 | 2.2727 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2538 | 2623 | 0 | 0 | 5.161 | 0.20644 | 7.6383 |  | -2.6383 | -12.7799 | - | 0 | -
dal13.sr03.rk15 | DAL13 | 3 | 15 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944788 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 18 | 23 | 5 | 0 | 5 | 0 | 23 | 28 | 50 | 27 | 8 | 0 | 35 | 0 | 0 | 15 | 23 | 23 | 23 | 0.1 | 2.0909 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2429 | 2428 | 0 | 0 | 4.857 | 0.17989 | 6.2961 |  | -1.2961 | -7.2051 | - | 0 | -
dal13.sr03.rk16 | DAL13 | 3 | 16 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944790 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 14 | 19 | 5 | 0 | 5 | 0 | 19 | 24 | 50 | 22 | 6 | 0 | 28 | 0 | 0 | 22 | 28 | 28 | 28 | 0.1 | 2.5455 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2555 | 2498 | 0 | 0 | 5.053 | 0.22968 | 6.4311 |  | -1.4311 | -6.2308 | - | 0 | -
dal13.sr03.rk17 | DAL13 | 3 | 17 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Power Limit | 50 | 1944792 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 0 | 46 | 46 | 46 | 46 | 0.1 | 4.1818 | 0 | Network - Power Limit | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk18 | DAL13 | 3 | 18 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944794 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 15 | 20 | 4 | 0 | 4 | 1 | 20 | 25 | 50 | 21 | 7 | 4 | 32 | 0 | 0 | 18 | 25 | 29 | 29 | 0.1 | 2.2727 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1684 | 1650 | 0 | 0 | 3.334 | 0.15876 | 5.0804 |  | -0.080381 | -0.5063 | - | 0 | -
dal13.sr03.rk19 | DAL13 | 3 | 19 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944796 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 18 | 23 | 7 | 0 | 7 | 0 | 25 | 30 | 50 | 23 | 11 | 0 | 34 | 0 | 0 | 16 | 27 | 27 | 27 | 0.1 | 2.4545 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2611 | 2780 | 0 | 0 | 5.391 | 0.23439 | 7.9693 |  | -2.9693 | -12.6682 | - | 0 | -
dal13.sr03.rk20 | DAL13 | 3 | 20 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944798 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 11 | 16 | 5 | 0 | 5 | 1 | 17 | 22 | 50 | 17 | 9 | 2 | 28 | 0 | 0 | 22 | 31 | 33 | 33 | 0.1 | 2.8182 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2028 | 2045 | 0 | 0 | 4.073 | 0.23959 | 6.7085 |  | -1.7085 | -7.1309 | - | 0 | -
dal13.sr03.rk21 | DAL13 | 3 | 21 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944800 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 17 | 22 | 4 | 0 | 4 | 0 | 21 | 26 | 50 | 27 | 7 | 0 | 34 | 0 | 0 | 16 | 23 | 23 | 23 | 0.1 | 2.0909 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2598 | 2419 | 0 | 0 | 5.017 | 0.18581 | 6.3177 |  | -1.3177 | -7.0915 | - | 0 | -
dal13.sr03.rk22 | DAL13 | 3 | 22 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944802 | 5 | 4 | L4 | Z6-375 | 2 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 17 | 22 | 6 | 0 | 6 | 0 | 23 | 28 | 50 | 25 | 9 | 0 | 34 | 0 | 0 | 16 | 25 | 25 | 25 | 0.1 | 2.2727 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2307 | 2360 | 0 | 0 | 4.667 | 0.18668 | 6.3471 |  | -1.3471 | -7.2162 | E | 0 | -
dal13.sr03.rk23 | DAL13 | 3 | 23 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944804 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 22 | 27 | 6 | 0 | 6 | 0 | 28 | 33 | 50 | 30 | 11 | 0 | 41 | 0 | 0 | 9 | 20 | 20 | 20 | 0.1 | 1.8182 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1578 | 1548 | 0 | 0 | 3.126 | 0.1042 | 4.2722 |  | 0.7278 | 6.9846 | S | 0 | -
dal13.sr03.rk24 | DAL13 | 3 | 24 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944806 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 13 | 18 | 9 | 0 | 9 | 0 | 22 | 27 | 50 | 19 | 18 | 0 | 37 | 0 | 0 | 13 | 31 | 31 | 31 | 0.1 | 2.8182 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1607 | 1556 | 0 | 0 | 3.163 | 0.16647 | 6.1595 |  | -1.1595 | -6.9652 | - | 0 | -
dal13.sr03.rk25 | DAL13 | 3 | 25 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944808 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 11 | 16 | 8 | 0 | 8 | 0 | 19 | 24 | 50 | 22 | 13 | 0 | 35 | 0 | 0 | 15 | 28 | 28 | 28 | 0.1 | 2.5455 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1525 | 1285 | 0 | 0 | 2.81 | 0.12773 | 4.4705 |  | 0.52955 | 4.1459 | - | 0 | -
dal13.sr03.rk26 | DAL13 | 3 | 26 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944810 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 19 | 24 | 4 | 0 | 4 | 1 | 24 | 29 | 50 | 24 | 9 | 1 | 34 | 0 | 0 | 16 | 25 | 26 | 26 | 0.1 | 2.2727 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2843 | 2850 | 0 | 0 | 5.693 | 0.23721 | 8.0651 |  | -3.0651 | -12.9215 | - | 0 | -
dal13.sr03.rk27 | DAL13 | 3 | 27 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944812 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 11 | 16 | 5 | 0 | 5 | 2 | 18 | 23 | 50 | 17 | 7 | 3 | 27 | 0 | 0 | 23 | 30 | 33 | 33 | 0.1 | 2.7273 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1922 | 1231 | 0 | 0 | 3.153 | 0.18547 | 5.0077 |  | -0.0077059 | -0.041548 | - | 0 | -
dal13.sr03.rk28 | DAL13 | 3 | 28 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Power Limit | 50 | 1944814 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 0 | 46 | 46 | 46 | 46 | 0.1 | 4.1818 | 0 | Network - Power Limit | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk29 | DAL13 | 3 | 29 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944816 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 9 | 14 | 0 | 0 | 0 | 1 | 10 | 15 | 50 | 23 | 0 | 1 | 24 | 0 | 0 | 26 | 26 | 27 | 27 | 0.1 | 2.3636 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1334 | 1462 | 0 | 0 | 2.796 | 0.12157 | 2.9176 |  | 2.0824 | 17.1302 | - | 0 | -
dal13.sr03.rk30 | DAL13 | 3 | 30 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944818 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 16 | 21 | 3 | 0 | 3 | 2 | 21 | 26 | 50 | 26 | 5 | 3 | 34 | 0 | 0 | 16 | 21 | 24 | 24 | 0.1 | 1.9091 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1673 | 1659 | 0 | 0 | 3.332 | 0.12815 | 4.3572 |  | 0.64277 | 5.0156 | - | 0 | -
dal13.sr03.rk31 | DAL13 | 3 | 31 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944820 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 17 | 22 | 4 | 0 | 4 | 0 | 21 | 26 | 50 | 26 | 7 | 0 | 33 | 0 | 0 | 17 | 24 | 24 | 24 | 0.1 | 2.1818 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1855 | 1814 | 0 | 0 | 3.669 | 0.14112 | 4.6568 |  | 0.34319 | 2.432 | - | 0 | -
dal13.sr03.rk32 | DAL13 | 3 | 32 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944822 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 20 | 25 | 7 | 0 | 7 | 0 | 27 | 32 | 50 | 26 | 7 | 0 | 33 | 0 | 0 | 17 | 24 | 24 | 24 | 0.1 | 2.1818 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2939 | 2896 | 0 | 0 | 5.835 | 0.22442 | 7.406 |  | -2.406 | -10.7207 | - | 0 | -
dal13.sr03.rk33 | DAL13 | 3 | 33 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944824 | 5 | 4 | L4 | Z6-375 | 3 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 3 | 8 | 7 | 0 | 7 | 1 | 11 | 16 | 50 | 11 | 13 | 2 | 26 | 0 | 0 | 24 | 37 | 39 | 39 | 0.1 | 3.3636 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 531 | 502 | 0 | 0 | 1.033 | 0.093909 | 2.4416 |  | 2.5584 | 27.243 | E | 0 | -
dal13.sr03.rk34 | DAL13 | 3 | 34 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944826 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 20 | 25 | 3 | 0 | 3 | 0 | 23 | 28 | 50 | 28 | 5 | 0 | 33 | 0 | 0 | 17 | 22 | 22 | 22 | 0.1 | 2 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 3354 | 3290 | 0 | 0 | 6.644 | 0.23729 | 7.8304 |  | -2.8304 | -11.9284 | S | 0 | -
dal13.sr03.rk35 | DAL13 | 3 | 35 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944828 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 12 | 17 | 1 | 0 | 1 | 0 | 13 | 18 | 50 | 18 | 1 | 0 | 19 | 0 | 0 | 31 | 32 | 32 | 32 | 0.1 | 2.9091 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1348 | 1333 | 0 | 0 | 2.681 | 0.14894 | 2.8299 |  | 2.1701 | 14.5696 | - | 0 | -
dal13.sr03.rk36 | DAL13 | 3 | 36 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944830 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 13 | 18 | 1 | 0 | 1 | 1 | 15 | 20 | 50 | 19 | 1 | 1 | 21 | 0 | 0 | 29 | 30 | 31 | 31 | 0.1 | 2.7273 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1464 | 1515 | 0 | 0 | 2.979 | 0.15679 | 3.2926 |  | 1.7074 | 10.8899 | - | 0 | -
dal13.sr03.rk37 | DAL13 | 3 | 37 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944832 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 10 | 15 | 8 | 0 | 8 | 0 | 18 | 23 | 50 | 18 | 17 | 0 | 35 | 0 | 0 | 15 | 32 | 32 | 32 | 0.1 | 2.9091 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1708 | 1281 | 0 | 0 | 2.989 | 0.16606 | 5.8119 |  | -0.81194 | -4.8896 | - | 0 | -
dal13.sr03.rk38 | DAL13 | 3 | 38 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944834 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 5 | 10 | 8 | 0 | 8 | 0 | 13 | 18 | 50 | 12 | 16 | 0 | 28 | 0 | 0 | 22 | 38 | 38 | 38 | 0.1 | 3.4545 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 762 | 703 | 0 | 0 | 1.465 | 0.12208 | 3.4183 |  | 1.5817 | 12.9556 | - | 0 | -
dal13.sr03.rk39 | DAL13 | 3 | 39 | 2 | 10G | Dual Path | Unsellable | Network | Aggregate | Power Limit | 50 | 1944836 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 0 | 46 | 46 | 46 | 46 | 0.1 | 4.1818 | 0 | Network - Power Limit | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk40 | DAL13 | 3 | 40 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944838 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 26 | 31 | 1 | 0 | 1 | 1 | 28 | 33 | 50 | 32 | 2 | 1 | 35 | 0 | 0 | 15 | 17 | 18 | 18 | 0.1 | 1.5455 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2726 | 2720 | 0 | 0 | 5.446 | 0.17019 | 5.9566 |  | -0.95656 | -5.6206 | - | 0 | -
dal13.sr03.rk41 | DAL13 | 3 | 41 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944840 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 37 | 42 | 0 | 0 | 0 | 1 | 38 | 43 | 50 | 42 | 0 | 1 | 43 | 0 | 0 | 7 | 7 | 8 | 8 | 0.1 | 0.63636 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 3853 | 3969 | 0 | 0 | 7.822 | 0.18624 | 8.0082 |  | -3.0082 | -16.1526 | - | 0 | -
dal13.sr03.rk42 | DAL13 | 3 | 42 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944842 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 19 | 24 | 7 | 0 | 7 | 0 | 26 | 31 | 50 | 26 | 14 | 0 | 40 | 0 | 0 | 10 | 24 | 24 | 24 | 0.1 | 2.1818 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2506 | 2461 | 0 | 0 | 4.967 | 0.19104 | 7.6415 |  | -2.6415 | -13.8273 | - | 0 | -
dal13.sr03.rk43 | DAL13 | 3 | 43 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944844 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 11 | 16 | 5 | 0 | 5 | 0 | 16 | 21 | 50 | 21 | 10 | 0 | 31 | 0 | 0 | 19 | 29 | 29 | 29 | 0.1 | 2.6364 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 1572 | 1535 | 0 | 0 | 3.107 | 0.14795 | 4.5865 |  | 0.41348 | 2.7947 | - | 0 | -
dal13.sr03.rk44 | DAL13 | 3 | 44 | 2 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944846 | 5 | 4 | L4 | Z6-375 | 4 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 22 | 27 | 1 | 0 | 1 | 0 | 23 | 28 | 50 | 27 | 2 | 0 | 29 | 0 | 0 | 21 | 23 | 23 | 23 | 0.1 | 2.0909 | 0 | Bare Metal - Power Limit | N | DAL13-102 | 2442 | 2471 | 0 | 0 | 4.913 | 0.18196 | 5.2769 |  | -0.27693 | -1.5219 | E | 0 | -
dal13.sr03.rk45 | DAL13 | 3 | 45 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944848 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 6 | 11 | 5 | 0 | 5 | 0 | 11 | 16 | 50 | 17 | 12 | 0 | 29 | 0 | 33 | 21 | 33 | 33 | 0 | 0.18 | 3 | 0 | Bare Metal - Live | N | DAL13-102 | 1887 | 1820 | 0 | 0 | 3.707 | 0.21806 | 6.3237 |  | 2.6763 | 12.2733 | S | 0 | -
dal13.sr03.rk46 | DAL13 | 3 | 46 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944850 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 9 | 14 | 3 | 0 | 3 | 0 | 12 | 17 | 50 | 23 | 6 | 0 | 29 | 0 | 27 | 21 | 27 | 27 | 0 | 0.18 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-102 | 2301 | 1953 | 0 | 0 | 4.254 | 0.18496 | 5.3637 |  | 3.6363 | 19.6601 | - | 0 | -
dal13.sr03.rk47 | DAL13 | 3 | 47 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944852 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 13 | 18 | 1 | 0 | 1 | 1 | 15 | 20 | 50 | 31 | 2 | 2 | 35 | 0 | 19 | 15 | 17 | 19 | 0 | 0.18 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 2496 | 2371 | 0 | 0 | 4.867 | 0.157 | 5.495 |  | 3.505 | 22.3248 | - | 0 | -
dal13.sr03.rk48 | DAL13 | 3 | 48 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944854 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 6 | 11 | 7 | 0 | 7 | 2 | 15 | 20 | 50 | 17 | 14 | 4 | 35 | 0 | 33 | 15 | 29 | 33 | 0 | 0.18 | 2.6364 | 0 | Bare Metal - Live | N | DAL13-102 | 1356 | 1259 | 0 | 0 | 2.615 | 0.15382 | 5.3838 |  | 3.6162 | 23.5086 | - | 0 | -
dal13.sr03.rk49 | DAL13 | 3 | 49 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944856 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 17 | 22 | 0 | 0 | 0 | 0 | 17 | 22 | 50 | 39 | 0 | 0 | 39 | 0 | 11 | 11 | 11 | 11 | 0 | 0.18 | 1 | 0 | Bare Metal - Live | N | DAL13-102 | 2908 | 2812 | 0 | 0 | 5.72 | 0.14667 | 5.72 |  | 3.28 | 22.3636 | - | 0 | -
dal13.sr03.rk50 | DAL13 | 3 | 50 | 2 | 25G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1944858 | 5 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 8 | 0 | 0 | 8 | 0 | 42 | 42 | 42 | 42 | 0 | 0.1 | 3.8182 | 0 | Network - Live | N | DAL13-102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk51 | DAL13 | 3 | 51 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944860 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 8 | 13 | 2 | 0 | 2 | 0 | 10 | 15 | 50 | 21 | 4 | 0 | 25 | 0 | 29 | 25 | 29 | 29 | 0 | 0.18 | 2.6364 | 0 | Bare Metal - Live | N | DAL13-102 | 1920 | 1502 | 0 | 0 | 3.422 | 0.16295 | 4.0738 |  | 4.9262 | 30.2309 | - | 0 | -
dal13.sr03.rk52 | DAL13 | 3 | 52 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944862 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 4 | 13 | 2 | 0 | 2 | 0 | 6 | 15 | 50 | 21 | 4 | 0 | 25 | 0 | 29 | 25 | 29 | 29 | 0 | 0.18 | 2.6364 | 0 | Bare Metal - Live | N | DAL13-102 | 1180 | 1131 | 0 | 0 | 2.311 | 0.11005 | 2.7512 |  | 6.2488 | 56.7828 | - | 0 | -
dal13.sr03.rk53 | DAL13 | 3 | 53 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944864 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 10 | 19 | 2 | 0 | 2 | 0 | 12 | 21 | 50 | 33 | 4 | 0 | 37 | 0 | 17 | 13 | 17 | 17 | 0 | 0.18 | 1.5455 | 0 | Bare Metal - Live | N | DAL13-102 | 2377 | 2343 | 0 | 0 | 4.72 | 0.14303 | 5.2921 |  | 3.7079 | 25.9237 | - | 0 | -
dal13.sr03.rk54 | DAL13 | 3 | 54 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944866 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 11 | 20 | 0 | 0 | 0 | 0 | 11 | 20 | 50 | 35 | 0 | 0 | 35 | 0 | 15 | 15 | 15 | 15 | 0 | 0.18 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-102 | 2193 | 2672 | 0 | 0 | 4.865 | 0.139 | 4.865 |  | 4.135 | 29.7482 | - | 0 | -
dal13.sr03.rk55 | DAL13 | 3 | 55 | 2 | 25G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944868 | 9 | 4 | L4 | Z6-375 | 5 | vlam - 11/10/2023 - Per Andy, setting this to Live. |  | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 5 | 0 | 0 | 5 | 0 | 45 | 45 | 45 | 45 | 0 | 0.18 | 4.0909 | 0 | Bare Metal - Live | N | DAL13-102 | 151 | 128 | 0 | 0 | 0.279 | 0.0558 | 0.279 |  | 8.721 | 156.2903 | E | 1 | -
dal13.sr03.rk56 | DAL13 | 3 | 56 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944870 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 41 | 46 | 1 | 0 | 1 | 0 | 42 | 47 | 50 | 46 | 1 | 0 | 47 | 0 | 0 | 3 | 4 | 4 | 4 | 0.18 | 0.36364 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 6466 | 6449 | 0 | 0 | 12.915 | 0.28076 | 13.1958 |  | -4.1958 | -14.9443 | S | 0 | -
dal13.sr03.rk57 | DAL13 | 3 | 57 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944872 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 29 | 34 | 7 | 0 | 7 | 3 | 39 | 44 | 50 | 34 | 7 | 3 | 44 | 0 | 0 | 6 | 13 | 16 | 16 | 0.18 | 1.1818 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 2762 | 2620 | 0 | 0 | 5.382 | 0.15829 | 6.9649 |  | 2.0351 | 12.8562 | - | 0 | -
dal13.sr03.rk58 | DAL13 | 3 | 58 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944874 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 18 | 23 | 4 | 0 | 4 | 16 | 38 | 43 | 50 | 23 | 4 | 16 | 43 | 0 | 0 | 7 | 11 | 27 | 27 | 0.18 | 1 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 2087 | 2108 | 0 | 0 | 4.195 | 0.18239 | 7.8428 |  | 1.1572 | 6.3445 | - | 0 | -
dal13.sr03.rk59 | DAL13 | 3 | 59 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944876 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 30 | 35 | 1 | 0 | 1 | 7 | 38 | 43 | 50 | 35 | 1 | 7 | 43 | 0 | 0 | 7 | 8 | 15 | 15 | 0.18 | 0.72727 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 5165 | 5180 | 0 | 0 | 10.345 | 0.29557 | 12.7096 |  | -3.7096 | -12.5505 | - | 0 | -
dal13.sr03.rk60 | DAL13 | 3 | 60 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944878 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 39 | 44 | 2 | 0 | 2 | 0 | 41 | 46 | 50 | 44 | 2 | 0 | 46 | 0 | 0 | 4 | 6 | 6 | 6 | 0.18 | 0.54545 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 6527 | 6516 | 0 | 0 | 13.043 | 0.29643 | 13.6359 |  | -4.6359 | -15.6389 | - | 0 | -
dal13.sr03.rk61 | DAL13 | 3 | 61 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Power Limit | 50 | 1944880 | 5 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 0 | 46 | 46 | 46 | 46 | 0.1 | 4.1818 | 0 | Network - Power Limit | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk62 | DAL13 | 3 | 62 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944882 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 41 | 46 | 0 | 0 | 0 | 1 | 42 | 47 | 50 | 46 | 0 | 1 | 47 | 0 | 0 | 3 | 3 | 4 | 4 | 0.18 | 0.27273 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 6794 | 6715 | 0 | 0 | 13.509 | 0.29367 | 13.8027 |  | -4.8027 | -16.3538 | - | 0 | -
dal13.sr03.rk63 | DAL13 | 3 | 63 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944884 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 38 | 43 | 1 | 0 | 1 | 2 | 41 | 46 | 50 | 43 | 1 | 2 | 46 | 0 | 0 | 4 | 5 | 7 | 7 | 0.18 | 0.45455 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 6359 | 6186 | 0 | 0 | 12.545 | 0.29174 | 13.4202 |  | -4.4202 | -15.1511 | - | 0 | -
dal13.sr03.rk64 | DAL13 | 3 | 64 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944886 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 38 | 43 | 0 | 0 | 0 | 0 | 38 | 43 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 7 | 7 | 7 | 7 | 0.18 | 0.63636 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 5790 | 5720 | 0 | 0 | 11.51 | 0.26767 | 11.51 |  | -2.51 | -9.3771 | - | 0 | -
dal13.sr03.rk65 | DAL13 | 3 | 65 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944888 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 40 | 45 | 0 | 0 | 0 | 1 | 41 | 46 | 50 | 45 | 0 | 1 | 46 | 0 | 0 | 4 | 4 | 5 | 5 | 0.18 | 0.36364 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 4710 | 4269 | 0 | 0 | 8.979 | 0.19953 | 9.1785 |  | -0.17853 | -0.89475 | - | 0 | -
dal13.sr03.rk66 | DAL13 | 3 | 66 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Power Limit | 50 | 1944890 | 9 | 4 | L4 | Z6-375 | 6 | vlam - 10/13/2022 - Set to Power Limit due to limited power in the zone and threshold being reached. |  | 39 | 44 | 1 | 0 | 1 | 1 | 41 | 46 | 50 | 44 | 1 | 1 | 46 | 0 | 0 | 4 | 5 | 6 | 6 | 0.18 | 0.45455 | 0 | Bare Metal - Power Limit | N | DAL13-103 | 3848 | 3855 | 0 | 0 | 7.703 | 0.17507 | 8.0531 |  | 0.94686 | 5.4085 | E | 0 | -
dal13.sr03.rk67 | DAL13 | 3 | 67 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944892 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 10 | 15 | 6 | 0 | 6 | 5 | 21 | 26 | 50 | 24 | 9 | 10 | 43 | 0 | 26 | 7 | 16 | 26 | 0 | 0.1 | 1.4545 | 0 | Compute - Live | N | DAL13-103 | 1865 | 1740 | 0 | 0 | 3.605 | 0.15021 | 6.459 |  | -1.459 | -9.7129 | S | 0 | -
dal13.sr03.rk68 | DAL13 | 3 | 68 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944894 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 12 | 17 | 15 | 0 | 15 | 2 | 29 | 34 | 50 | 23 | 17 | 4 | 44 | 0 | 27 | 6 | 23 | 27 | 0 | 0.1 | 2.0909 | 0 | Compute - Live | N | DAL13-103 | 2238 | 2508 | 0 | 0 | 4.746 | 0.20635 | 9.0793 |  | -4.0793 | -19.7691 | - | 0 | -
dal13.sr03.rk69 | DAL13 | 3 | 69 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944896 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 19 | 24 | 7 | 0 | 7 | 2 | 28 | 33 | 50 | 30 | 10 | 4 | 44 | 0 | 20 | 6 | 16 | 20 | 0 | 0.1 | 1.4545 | 0 | Compute - Live | N | DAL13-103 | 2607 | 2525 | 0 | 0 | 5.132 | 0.17107 | 7.5269 |  | -2.5269 | -14.7716 | - | 0 | -
dal13.sr03.rk70 | DAL13 | 3 | 70 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944898 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 12 | 17 | 15 | 0 | 15 | 2 | 29 | 34 | 50 | 23 | 16 | 4 | 43 | 0 | 27 | 7 | 23 | 27 | 0 | 0.1 | 2.0909 | 0 | Compute - Live | N | DAL13-103 | 2290 | 2211 | 0 | 0 | 4.501 | 0.1957 | 8.4149 |  | -3.4149 | -17.4501 | - | 0 | -
dal13.sr03.rk71 | DAL13 | 3 | 71 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944900 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 18 | 23 | 12 | 0 | 12 | 4 | 34 | 39 | 50 | 25 | 16 | 6 | 47 | 0 | 25 | 3 | 19 | 25 | 0 | 0.1 | 1.7273 | 0 | Compute - Live | N | DAL13-103 | 2425 | 2427 | 0 | 0 | 4.852 | 0.19408 | 9.1218 |  | -4.1218 | -21.2374 | - | 0 | -
dal13.sr03.rk72 | DAL13 | 3 | 72 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1944902 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk73 | DAL13 | 3 | 73 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944904 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 32 | 37 | 5 | 0 | 5 | 1 | 38 | 43 | 50 | 39 | 5 | 1 | 45 | 0 | 11 | 5 | 10 | 11 | 0 | 0.1 | 0.90909 | 0 | Compute - Live | N | DAL13-103 | 3367 | 3326 | 0 | 0 | 6.693 | 0.17162 | 7.7227 |  | -2.7227 | -15.8651 | - | 0 | -
dal13.sr03.rk74 | DAL13 | 3 | 74 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944906 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 6 | 11 | 21 | 1 | 20 | 6 | 33 | 38 | 50 | 14 | 21 | 9 | 45 | 1 | 36 | 5 | 26 | 35 | 0 | 0.1 | 2.3636 | 0.13636 | Compute - Live | N | DAL13-103 | 2022 | 2039 | 0 | 0 | 4.061 | 0.29007 | 13.0532 |  | -8.0532 | -27.7629 | - | 0 | -
dal13.sr03.rk75 | DAL13 | 3 | 75 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944908 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 8 | 13 | 12 | 0 | 12 | 14 | 34 | 39 | 50 | 16 | 14 | 16 | 46 | 0 | 34 | 4 | 18 | 34 | 0 | 0.1 | 1.6364 | 0 | Compute - Live | N | DAL13-103 | 1702 | 1681 | 0 | 0 | 3.383 | 0.21144 | 9.7261 |  | -4.7261 | -22.3523 | - | 0 | -
dal13.sr03.rk76 | DAL13 | 3 | 76 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944910 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 8 | 13 | 23 | 0 | 23 | 3 | 34 | 39 | 50 | 15 | 24 | 3 | 42 | 0 | 35 | 8 | 32 | 35 | 0 | 0.1 | 2.9091 | 0 | Compute - Live | N | DAL13-103 | 2570 | 2713 | 0 | 0 | 5.283 | 0.3522 | 14.7924 |  | -9.7924 | -27.8035 | - | 0 | -
dal13.sr03.rk77 | DAL13 | 3 | 77 | 3 | 10G | Dual Path | Sellable | Compute | Hybrid | Live | 50 | 1944912 | 5 | 4 | L4 | Z5-375 | 7 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 8 | 13 | 15 | 0 | 15 | 1 | 24 | 29 | 50 | 22 | 22 | 2 | 46 | 0 | 28 | 4 | 26 | 28 | 0 | 0.1 | 2.3636 | 0 | Compute - Live | N | DAL13-103 | 2171 | 2307 | 0 | 0 | 4.478 | 0.20355 | 9.3631 |  | -4.3631 | -21.4355 | E | 0 | -
dal13.sr03.rk78 | DAL13 | 3 | 78 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944914 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 12 | 17 | 5 | 0 | 5 | 14 | 31 | 36 | 50 | 21 | 10 | 14 | 45 | 0 | 29 | 5 | 15 | 29 | 0 | 0.154 | 1.3636 | 0 | Bare Metal - Live | N | DAL13-103 | 2230 | 2282 | 0 | 0 | 4.512 | 0.21486 | 9.6686 |  | -1.9686 | -9.1622 | S | 0 | -
dal13.sr03.rk79 | DAL13 | 3 | 79 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944916 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 12 | 17 | 16 | 0 | 16 | 1 | 29 | 34 | 50 | 24 | 19 | 2 | 45 | 0 | 26 | 5 | 24 | 26 | 0 | 0.154 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-103 | 3271 | 3064 | 0 | 0 | 6.335 | 0.26396 | 11.8781 |  | -4.1781 | -15.8287 | - | 0 | -
dal13.sr03.rk80 | DAL13 | 3 | 80 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944918 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 15 | 20 | 3 | 0 | 3 | 2 | 20 | 25 | 50 | 34 | 8 | 5 | 47 | 0 | 16 | 3 | 11 | 16 | 0 | 0.154 | 1 | 0 | Bare Metal - Live | N | DAL13-103 | 2789 | 2466 | 0 | 0 | 5.255 | 0.15456 | 7.2643 |  | 0.43574 | 2.8192 | - | 0 | -
dal13.sr03.rk81 | DAL13 | 3 | 81 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944920 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 21 | 26 | 0 | 0 | 0 | 1 | 22 | 27 | 50 | 42 | 0 | 2 | 44 | 0 | 8 | 6 | 6 | 8 | 0 | 0.154 | 0.54545 | 0 | Bare Metal - Live | N | DAL13-103 | 3209 | 3644 | 0 | 0 | 6.853 | 0.16317 | 7.1793 |  | 0.52067 | 3.191 | - | 0 | -
dal13.sr03.rk82 | DAL13 | 3 | 82 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944922 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 18 | 23 | 3 | 0 | 3 | 10 | 31 | 36 | 50 | 32 | 3 | 13 | 48 | 0 | 18 | 2 | 5 | 18 | 0 | 0.154 | 0.45455 | 0 | Bare Metal - Live | N | DAL13-103 | 3182 | 3380 | 0 | 0 | 6.562 | 0.20506 | 9.843 |  | -2.143 | -10.4505 | - | 0 | -
dal13.sr03.rk83 | DAL13 | 3 | 83 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1944924 | 5 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk84 | DAL13 | 3 | 84 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944926 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 17 | 22 | 10 | 0 | 10 | 0 | 27 | 32 | 50 | 28 | 13 | 0 | 41 | 0 | 22 | 9 | 22 | 22 | 0 | 0.154 | 2 | 0 | Bare Metal - Live | N | DAL13-103 | 2589 | 2590 | 0 | 0 | 5.179 | 0.18496 | 7.5835 |  | 0.11646 | 0.62966 | - | 0 | -
dal13.sr03.rk85 | DAL13 | 3 | 85 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944928 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 24 | 29 | 16 | 0 | 16 | 1 | 41 | 46 | 50 | 29 | 16 | 1 | 46 | 0 | 21 | 4 | 20 | 21 | 0 | 0.154 | 1.8182 | 0 | Bare Metal - Live | N | DAL13-103 | 3909 | 4249 | 0 | 0 | 8.158 | 0.28131 | 12.9403 |  | -5.2403 | -18.6281 | - | 0 | -
dal13.sr03.rk86 | DAL13 | 3 | 86 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944930 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 6 | 11 | 16 | 0 | 16 | 9 | 31 | 36 | 50 | 11 | 21 | 11 | 43 | 0 | 39 | 7 | 28 | 39 | 0 | 0.154 | 2.5455 | 0 | Bare Metal - Live | N | DAL13-103 | 1085 | 1105 | 0 | 0 | 2.19 | 0.19909 | 8.5609 |  | -0.86091 | -4.3242 | - | 0 | -
dal13.sr03.rk87 | DAL13 | 3 | 87 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944932 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 24 | 29 | 5 | 0 | 5 | 10 | 39 | 44 | 50 | 30 | 5 | 11 | 46 | 0 | 20 | 4 | 9 | 20 | 0 | 0.154 | 0.81818 | 0 | Bare Metal - Live | N | DAL13-103 | 2502 | 2537 | 0 | 0 | 5.039 | 0.16797 | 7.7265 |  | -0.026467 | -0.15757 | - | 0 | -
dal13.sr03.rk88 | DAL13 | 3 | 88 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944934 | 7.7 | 4 | L4 | Z5-375 | 8 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 16 | 21 | 5 | 0 | 5 | 7 | 28 | 33 | 50 | 25 | 12 | 7 | 44 | 0 | 25 | 6 | 18 | 25 | 0 | 0.154 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-103 | 1920 | 1938 | 0 | 0 | 3.858 | 0.15432 | 6.7901 |  | 0.90992 | 5.8963 | E | 0 | -
dal13.sr03.rk89 | DAL13 | 3 | 89 | 3 | 10G | Dual Path | Sellable | Network | Ded. Firewall | Live | 50 | 1944936 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 12 | 0 | 0 | 12 | 0 | 38 | 38 | 38 | 38 | 0 | 0.12 | 3.4545 | 0 | Network - Live | N | DAL13-103 | 847 | 644 | 0 | 0 | 1.491 | 0.12425 | 1.491 |  | 4.509 | 36.2897 | S | 0 | -
dal13.sr03.rk90 | DAL13 | 3 | 90 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944938 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 0 | 5 | 23 | 0 | 23 | 0 | 23 | 28 | 50 | 5 | 44 | 0 | 49 | 0 | 45 | 1 | 45 | 45 | 0 | 0.12 | 4.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 2061 | 2376 | 0 | 0 | 4.437 | 0.8874 | 43.4826 |  | -37.4826 | -42.2387 | - | 1 | -
dal13.sr03.rk91 | DAL13 | 3 | 91 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944940 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 17 | 22 | 17 | 0 | 17 | 2 | 36 | 41 | 50 | 22 | 17 | 4 | 43 | 0 | 28 | 7 | 24 | 28 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-103 | 3579 | 3696 | 0 | 0 | 7.275 | 0.33068 | 14.2193 |  | -8.2193 | -24.8557 | - | 0 | -
dal13.sr03.rk92 | DAL13 | 3 | 92 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944942 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 0 | 5 | 40 | 0 | 40 | 0 | 40 | 45 | 50 | 5 | 42 | 0 | 47 | 0 | 45 | 3 | 45 | 45 | 0 | 0.12 | 4.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 2149 | 2217 | 0 | 0 | 4.366 | 0.8732 | 41.0404 |  | -35.0404 | -40.1287 | - | 1 | -
dal13.sr03.rk93 | DAL13 | 3 | 93 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944944 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 4 | 9 | 25 | 0 | 25 | 2 | 31 | 36 | 50 | 12 | 25 | 4 | 41 | 0 | 38 | 9 | 34 | 38 | 0 | 0.12 | 3.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 1975 | 1728 | 0 | 0 | 3.703 | 0.30858 | 12.6519 |  | -6.6519 | -21.5563 | - | 0 | -
dal13.sr03.rk94 | DAL13 | 3 | 94 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1944946 | 5 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk95 | DAL13 | 3 | 95 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944948 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 13 | 18 | 6 | 0 | 6 | 2 | 21 | 26 | 50 | 21 | 10 | 6 | 37 | 0 | 29 | 13 | 23 | 29 | 0 | 0.12 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 2143 | 2087 | 0 | 0 | 4.23 | 0.20143 | 7.4529 |  | -1.4529 | -7.2128 | - | 0 | -
dal13.sr03.rk96 | DAL13 | 3 | 96 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944950 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 5 | 10 | 10 | 0 | 10 | 10 | 25 | 30 | 50 | 10 | 10 | 10 | 30 | 0 | 40 | 20 | 30 | 40 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-103 | 814 | 862 | 0 | 0 | 1.676 | 0.1676 | 5.028 |  | 0.972 | 5.7995 | - | 0 | -
dal13.sr03.rk97 | DAL13 | 3 | 97 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944952 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 10 | 15 | 18 | 0 | 18 | 2 | 30 | 35 | 50 | 16 | 23 | 2 | 41 | 0 | 34 | 9 | 32 | 34 | 0 | 0.12 | 2.9091 | 0 | Bare Metal - Live | N | DAL13-103 | 1973 | 2129 | 0 | 0 | 4.102 | 0.25638 | 10.5114 |  | -4.5114 | -17.5968 | - | 0 | -
dal13.sr03.rk98 | DAL13 | 3 | 98 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944954 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 17 | 22 | 12 | 0 | 12 | 3 | 32 | 37 | 50 | 23 | 12 | 3 | 38 | 0 | 27 | 12 | 24 | 27 | 0 | 0.12 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-103 | 1820 | 1777 | 0 | 0 | 3.597 | 0.15639 | 5.9429 |  | 0.05713 | 0.3653 | - | 0 | -
dal13.sr03.rk99 | DAL13 | 3 | 99 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944956 | 6 | 4 | L4 | Z5-375 | 9 | ccoronado - Updating serial per Sean Adams. Ticket: 138819034 |  | 17 | 22 | 7 | 0 | 7 | 3 | 27 | 32 | 50 | 25 | 7 | 9 | 41 | 0 | 25 | 9 | 16 | 25 | 0 | 0.12 | 1.4545 | 0 | Bare Metal - Live | N | DAL13-103 | 2467 | 1851 | 0 | 0 | 4.318 | 0.17272 | 7.0815 |  | -1.0815 | -6.2617 | E | 0 | -
dal13.sr03.rk100 | DAL13 | 3 | 100 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944958 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 10 | 15 | 15 | 0 | 15 | 1 | 26 | 31 | 50 | 17 | 19 | 4 | 40 | 0 | 33 | 10 | 29 | 33 | 0 | 0.12 | 2.6364 | 0 | Bare Metal - Live | N | DAL13-103 | 1394 | 1723 | 0 | 0 | 3.117 | 0.18335 | 7.3341 |  | -1.3341 | -7.2762 | S | 0 | -
dal13.sr03.rk101 | DAL13 | 3 | 101 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944960 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 8 | 13 | 9 | 0 | 9 | 1 | 18 | 23 | 50 | 18 | 22 | 2 | 42 | 0 | 32 | 8 | 30 | 32 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-103 | 1606 | 1541 | 0 | 0 | 3.147 | 0.17483 | 7.343 |  | -1.343 | -7.6816 | - | 0 | -
dal13.sr03.rk102 | DAL13 | 3 | 102 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944962 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 8 | 13 | 17 | 0 | 17 | 4 | 29 | 34 | 50 | 14 | 20 | 5 | 39 | 0 | 36 | 11 | 31 | 36 | 0 | 0.12 | 2.8182 | 0 | Bare Metal - Live | N | DAL13-103 | 1568 | 1725 | 0 | 0 | 3.293 | 0.23521 | 9.1734 |  | -3.1734 | -13.4913 | - | 0 | -
dal13.sr03.rk103 | DAL13 | 3 | 103 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944964 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 15 | 20 | 6 | 0 | 6 | 2 | 23 | 28 | 50 | 22 | 9 | 3 | 34 | 0 | 28 | 16 | 25 | 28 | 0 | 0.12 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-103 | 1962 | 1765 | 0 | 0 | 3.727 | 0.16941 | 5.7599 |  | 0.24009 | 1.4172 | - | 0 | -
dal13.sr03.rk104 | DAL13 | 3 | 104 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944966 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 15 | 20 | 9 | 0 | 9 | 1 | 25 | 30 | 50 | 22 | 12 | 1 | 35 | 0 | 28 | 15 | 27 | 28 | 0 | 0.12 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-103 | 1883 | 1834 | 0 | 0 | 3.717 | 0.16895 | 5.9134 |  | 0.086591 | 0.51251 | - | 0 | -
dal13.sr03.rk105 | DAL13 | 3 | 105 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1944968 | 5 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk106 | DAL13 | 3 | 106 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944970 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 11 | 16 | 8 | 0 | 8 | 0 | 19 | 24 | 50 | 19 | 11 | 0 | 30 | 0 | 31 | 20 | 31 | 31 | 0 | 0.12 | 2.8182 | 0 | Bare Metal - Live | N | DAL13-103 | 1513 | 1456 | 0 | 0 | 2.969 | 0.15626 | 4.6879 |  | 1.3121 | 8.3968 | - | 0 | -
dal13.sr03.rk107 | DAL13 | 3 | 107 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944972 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 3 | 8 | 7 | 0 | 7 | 1 | 11 | 16 | 50 | 8 | 10 | 4 | 22 | 0 | 42 | 28 | 38 | 42 | 0 | 0.12 | 3.4545 | 0 | Bare Metal - Live | N | DAL13-103 | 673 | 630 | 0 | 0 | 1.303 | 0.16287 | 3.5832 |  | 2.4168 | 14.8381 | - | 0 | -
dal13.sr03.rk108 | DAL13 | 3 | 108 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944974 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 10 | 15 | 12 | 0 | 12 | 0 | 22 | 27 | 50 | 20 | 20 | 0 | 40 | 0 | 30 | 10 | 30 | 30 | 0 | 0.12 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-103 | 1980 | 2317 | 0 | 0 | 4.297 | 0.21485 | 8.594 |  | -2.594 | -12.0735 | - | 0 | -
dal13.sr03.rk109 | DAL13 | 3 | 109 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944976 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 2 | 7 | 21 | 0 | 21 | 4 | 27 | 32 | 50 | 8 | 25 | 8 | 41 | 0 | 42 | 9 | 34 | 42 | 0 | 0.12 | 3.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 1243 | 1107 | 0 | 0 | 2.35 | 0.29375 | 12.0438 |  | -6.0438 | -20.5745 | - | 0 | -
dal13.sr03.rk110 | DAL13 | 3 | 110 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944978 | 6 | 4 | L4 | Z5-375 | 10 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 8 | 13 | 8 | 0 | 8 | 11 | 27 | 32 | 50 | 14 | 10 | 13 | 37 | 0 | 36 | 13 | 23 | 36 | 0 | 0.12 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 1162 | 1102 | 0 | 0 | 2.264 | 0.16171 | 5.9834 |  | 0.016571 | 0.10247 | E | 0 | -
dal13.sr03.rk111 | DAL13 | 3 | 111 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944980 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 14 | 19 | 6 | 0 | 6 | 5 | 25 | 30 | 50 | 20 | 9 | 7 | 36 | 0 | 30 | 14 | 23 | 30 | 0 | 0.1 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 1366 | 1330 | 0 | 0 | 2.696 | 0.1348 | 4.8528 |  | 0.1472 | 1.092 | S | 0 | -
dal13.sr03.rk112 | DAL13 | 3 | 112 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944982 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 18 | 23 | 4 | 0 | 4 | 3 | 25 | 30 | 50 | 28 | 6 | 4 | 38 | 0 | 22 | 12 | 18 | 22 | 0 | 0.1 | 1.6364 | 0 | Bare Metal - Live | N | DAL13-103 | 2044 | 2515 | 0 | 0 | 4.559 | 0.16282 | 6.1872 |  | -1.1872 | -7.2915 | - | 0 | -
dal13.sr03.rk113 | DAL13 | 3 | 113 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944984 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 2 | 7 | 16 | 0 | 16 | 1 | 19 | 24 | 50 | 9 | 29 | 2 | 40 | 0 | 41 | 10 | 39 | 41 | 0 | 0.1 | 3.5455 | 0 | Bare Metal - Live | N | DAL13-103 | 1023 | 1006 | 0 | 0 | 2.029 | 0.22544 | 9.0178 |  | -4.0178 | -17.8216 | - | 0 | -
dal13.sr03.rk114 | DAL13 | 3 | 114 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944986 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 15 | 20 | 4 | 0 | 4 | 1 | 20 | 25 | 50 | 25 | 10 | 1 | 36 | 0 | 25 | 14 | 24 | 25 | 0 | 0.1 | 2.1818 | 0 | Bare Metal - Live | N | DAL13-103 | 1653 | 1587 | 0 | 0 | 3.24 | 0.1296 | 4.6656 |  | 0.3344 | 2.5802 | - | 0 | -
dal13.sr03.rk115 | DAL13 | 3 | 115 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944988 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 15 | 20 | 12 | 0 | 12 | 2 | 29 | 34 | 50 | 20 | 21 | 3 | 44 | 0 | 30 | 6 | 27 | 30 | 0 | 0.1 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-103 | 1529 | 1397 | 0 | 0 | 2.926 | 0.1463 | 6.4372 |  | -1.4372 | -9.8237 | - | 0 | -
dal13.sr03.rk116 | DAL13 | 3 | 116 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1944990 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk117 | DAL13 | 3 | 117 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944992 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 14 | 19 | 15 | 0 | 15 | 0 | 29 | 34 | 50 | 21 | 22 | 0 | 43 | 0 | 29 | 7 | 29 | 29 | 0 | 0.1 | 2.6364 | 0 | Bare Metal - Live | N | DAL13-103 | 3390 | 3533 | 0 | 0 | 6.923 | 0.32967 | 14.1757 |  | -9.1757 | -27.8332 | - | 0 | -
dal13.sr03.rk118 | DAL13 | 3 | 118 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944994 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 3 | 8 | 8 | 0 | 8 | 6 | 17 | 22 | 50 | 9 | 13 | 14 | 36 | 0 | 41 | 14 | 27 | 41 | 0 | 0.1 | 2.4545 | 0 | Bare Metal - Live | N | DAL13-103 | 1137 | 1237 | 0 | 0 | 2.374 | 0.26378 | 9.496 |  | -4.496 | -17.0447 | - | 0 | -
dal13.sr03.rk119 | DAL13 | 3 | 119 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944996 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 5 | 10 | 14 | 0 | 14 | 3 | 22 | 27 | 50 | 16 | 16 | 9 | 41 | 0 | 34 | 9 | 25 | 34 | 0 | 0.1 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-103 | 1240 | 1335 | 0 | 0 | 2.575 | 0.16094 | 6.5984 |  | -1.5984 | -9.932 | - | 0 | -
dal13.sr03.rk120 | DAL13 | 3 | 120 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1944998 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 2 | 7 | 10 | 0 | 10 | 0 | 12 | 17 | 50 | 8 | 19 | 0 | 27 | 0 | 42 | 23 | 42 | 42 | 0 | 0.1 | 3.8182 | 0 | Bare Metal - Live | N | DAL13-103 | 646 | 650 | 0 | 0 | 1.296 | 0.162 | 4.374 |  | 0.626 | 3.8642 | - | 0 | -
dal13.sr03.rk121 | DAL13 | 3 | 121 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945000 | 5 | 4 | L4 | Z5-375 | 11 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 6 | 11 | 6 | 0 | 6 | 2 | 14 | 19 | 50 | 15 | 9 | 5 | 29 | 0 | 35 | 21 | 30 | 35 | 0 | 0.1 | 2.7273 | 0 | Bare Metal - Live | N | DAL13-103 | 999 | 975 | 0 | 0 | 1.974 | 0.1316 | 3.8164 |  | 1.1836 | 8.9939 | E | 0 | -
dal13.sr03.rk122 | DAL13 | 3 | 122 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945002 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 4 | 10 | 2 | 0 | 2 | 0 | 5 | 12 | 50 | 10 | 2 | 0 | 12 | 0 | 40 | 38 | 40 | 40 | 0 | 0.1 | 3.6364 | 0 | Bare Metal - Live | N | DAL13-103 | 462 | 422 | 0 | 0 | 0.884 | 0.0884 | 1.0608 |  | 3.9392 | 44.5611 | S | 0 | -
dal13.sr03.rk123 | DAL13 | 3 | 123 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945004 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 5 | 7 | 0 | 7 | 2 | 9 | 14 | 50 | 5 | 18 | 8 | 31 | 0 | 45 | 19 | 37 | 45 | 0 | 0.1 | 3.3636 | 0 | Bare Metal - Live | N | DAL13-103 | 865 | 829 | 0 | 0 | 1.694 | 0.3388 | 10.5028 |  | -5.5028 | -16.242 | - | 1 | -
dal13.sr03.rk124 | DAL13 | 3 | 124 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945006 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 1 | 6 | 4 | 0 | 4 | 3 | 8 | 13 | 50 | 7 | 16 | 12 | 35 | 0 | 43 | 15 | 31 | 43 | 0 | 0.1 | 2.8182 | 0 | Bare Metal - Live | N | DAL13-103 | 1239 | 1111 | 0 | 0 | 2.35 | 0.33571 | 11.75 |  | -6.75 | -20.1064 | - | 0 | -
dal13.sr03.rk125 | DAL13 | 3 | 125 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945008 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 4 | 9 | 7 | 0 | 7 | 2 | 13 | 18 | 50 | 9 | 20 | 8 | 37 | 0 | 41 | 13 | 33 | 41 | 0 | 0.1 | 3 | 0 | Bare Metal - Live | N | DAL13-103 | 1063 | 1179 | 0 | 0 | 2.242 | 0.24911 | 9.2171 |  | -4.2171 | -16.9286 | - | 0 | -
dal13.sr03.rk126 | DAL13 | 3 | 126 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945010 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 1 | 6 | 7 | 0 | 7 | 2 | 10 | 15 | 50 | 7 | 14 | 6 | 27 | 0 | 43 | 23 | 37 | 43 | 0 | 0.1 | 3.3636 | 0 | Bare Metal - Live | N | DAL13-103 | 896 | 1385 | 0 | 0 | 2.281 | 0.32586 | 8.7981 |  | -3.7981 | -11.6559 | - | 0 | -
dal13.sr03.rk127 | DAL13 | 3 | 127 | 3 | 10G | Dual Path | Unsellable | Network | Aggregate | Live | 50 | 1945012 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 4 | 0 | 0 | 4 | 0 | 46 | 46 | 46 | 46 | 0 | 0.1 | 4.1818 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 5 | 0 | - | 0 | -
dal13.sr03.rk128 | DAL13 | 3 | 128 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945014 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 16 | 21 | 3 | 0 | 3 | 3 | 22 | 27 | 50 | 22 | 8 | 3 | 33 | 0 | 28 | 17 | 25 | 28 | 0 | 0.1 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-103 | 1485 | 1439 | 0 | 0 | 2.924 | 0.13291 | 4.386 |  | 0.614 | 4.6197 | - | 0 | -
dal13.sr03.rk129 | DAL13 | 3 | 129 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945016 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 4 | 9 | 8 | 0 | 8 | 8 | 20 | 25 | 50 | 10 | 11 | 17 | 38 | 0 | 40 | 12 | 23 | 40 | 0 | 0.1 | 2.0909 | 0 | Bare Metal - Live | N | DAL13-103 | 1458 | 1455 | 0 | 0 | 2.913 | 0.2913 | 11.0694 |  | -6.0694 | -20.8356 | - | 0 | -
dal13.sr03.rk130 | DAL13 | 3 | 130 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945018 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 9 | 14 | 7 | 0 | 7 | 7 | 23 | 28 | 50 | 18 | 19 | 7 | 44 | 0 | 32 | 6 | 25 | 32 | 0 | 0.1 | 2.2727 | 0 | Bare Metal - Live | N | DAL13-103 | 1665 | 1675 | 0 | 0 | 3.34 | 0.18556 | 8.1644 |  | -3.1644 | -17.0539 | - | 0 | -
dal13.sr03.rk131 | DAL13 | 3 | 131 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945020 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 3 | 8 | 7 | 0 | 7 | 3 | 13 | 18 | 50 | 11 | 16 | 6 | 33 | 0 | 39 | 17 | 33 | 39 | 0 | 0.1 | 3 | 0 | Bare Metal - Live | N | DAL13-103 | 1159 | 984 | 0 | 0 | 2.143 | 0.19482 | 6.429 |  | -1.429 | -7.335 | - | 0 | -
dal13.sr03.rk132 | DAL13 | 3 | 132 | 3 | 10G | Dual Path | Sellable | Bare Metal | Bare Metal | Live | 50 | 1945022 | 5 | 4 | L4 | Z5-375 | 12 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 6 | 11 | 8 | 0 | 8 | 2 | 16 | 21 | 50 | 11 | 17 | 6 | 34 | 0 | 39 | 16 | 33 | 39 | 0 | 0.1 | 3 | 0 | Bare Metal - Live | N | DAL13-103 | 1503 | 1388 | 0 | 0 | 2.891 | 0.26282 | 8.9358 |  | -3.9358 | -14.9754 | E | 0 | -
dal13.sr03.rk133 | DAL13 | 3 | 133 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 1945024 | 20 | 4 | L4 | Z4-375 | 13 | vlam - 8/19/22 - Allocated to NG for Z16 Integration and Staging per DCL-3328 |  | 16 | 21 | 3 | 0 | 3 | 4 | 16 | 28 | 50 | 21 | 5 | 10 | 36 | 0 | 29 | 14 | 19 | 29 | 0 | 0.4 | 1.7273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr03.rk134 | DAL13 | 3 | 134 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945026 | 20 | 4 | L4 | Z4-375 | 13 | vlam - 8/19/22 - Allocated to NG for Z16 Integration and Staging per DCL-3328 |  | 0 | 2 | 4 | 0 | 4 | 3 | 0 | 9 | 50 | 2 | 6 | 7 | 15 | 0 | 48 | 35 | 41 | 48 | 0 | 0.4 | 3.7273 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk135 | DAL13 | 3 | 135 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 1945028 | 20 | 4 | L4 | Z4-375 | 13 | vlam - 8/19/22 - Allocated to NG for Z16 Integration and Staging per DCL-3328 |  | 11 | 21 | 0 | 0 | 0 | 4 | 13 | 25 | 50 | 23 | 0 | 18 | 41 | 0 | 27 | 9 | 9 | 27 | 0 | 0.4 | 0.81818 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr03.rk136 | DAL13 | 3 | 136 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945030 | 20 | 4 | L4 | Z4-375 | 13 | vlam - 8/19/22 - Allocated to NG for Z16 Integration and Staging per DCL-3328 |  | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 6 | 50 | 2 | 0 | 7 | 9 | 0 | 48 | 41 | 41 | 48 | 0 | 0.4 | 3.7273 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk137 | DAL13 | 3 | 137 | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | Unknown | 50 | 3549089 |  | Unknown | Unknown | Unknown |  | ccoronado - Updating SL tag per Joey Phan. Ticket: 160941015 |  | 0 | 0 | 30 | 0 | 30 | 0 | 26 | 30 | 50 | 0 | 32 | 0 | 32 | 0 | 50 | 18 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Unknown - Unknown | N | DAL13-10Unknown | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | - | 0 | -
dal13.sr03.rk138 | DAL13 | 3 | 138 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945034 | 20 | 4 | L4 | Z4-375 | 13 | vlam - 5/15/2024 - Allocated to QZ2 per DCL-3079. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk139 | DAL13 | 3 | 139 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945036 | 0 | 4 | L4 | Z4-375 | 13 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk140 | DAL13 | 3 | 140 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945038 | 0 | 4 | L4 | Z4-375 | 13 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk141 | DAL13 | 3 | 141 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945040 | 0 | 4 | L4 | Z4-375 | 13 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk142 | DAL13 | 3 | 142 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945042 | 0 | 4 | L4 | Z4-375 | 13 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk143 | DAL13 | 3 | 143 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945044 | 0 | 4 | L4 | Z4-375 | 13 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 5 | -
dal13.sr03.rk144 | DAL13 | 3 | 144 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945046 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr03.rk145 | DAL13 | 3 | 145 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945048 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk146 | DAL13 | 3 | 146 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945050 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk147 | DAL13 | 3 | 147 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945052 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk148 | DAL13 | 3 | 148 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945054 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk149 | DAL13 | 3 | 149 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945056 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk150 | DAL13 | 3 | 150 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945058 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk151 | DAL13 | 3 | 151 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945060 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 8 | -
dal13.sr03.rk152 | DAL13 | 3 | 152 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945062 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 9 | -
dal13.sr03.rk153 | DAL13 | 3 | 153 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945064 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 10 | -
dal13.sr03.rk154 | DAL13 | 3 | 154 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945066 | 0 | 4 | L4 | Z4-375 | 14 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 11 | dal13.sr03.rk144 - dal13.sr03.rk154
dal13.sr03.rk155 | DAL13 | 3 | 155 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945068 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr03.rk156 | DAL13 | 3 | 156 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945070 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk157 | DAL13 | 3 | 157 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945072 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk158 | DAL13 | 3 | 158 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945074 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk159 | DAL13 | 3 | 159 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945076 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk160 | DAL13 | 3 | 160 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945078 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk161 | DAL13 | 3 | 161 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945080 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 50 | 0 | 0 | 20 | 20 | 0 | 0 | 30 | 30 | 50 | 50 | 0 | 2.7273 | 0 | Unallocated - Power Limit | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk162 | DAL13 | 3 | 162 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945082 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 50 | 0 | 0 | 16 | 16 | 0 | 0 | 34 | 34 | 50 | 50 | 0 | 3.0909 | 0 | Unallocated - Power Limit | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 8 | -
dal13.sr03.rk163 | DAL13 | 3 | 163 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945084 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | 50 | 0 | 0 | 6 | 6 | 0 | 0 | 44 | 44 | 50 | 50 | 0 | 4 | 0 | Unallocated - Power Limit | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 9 | -
dal13.sr03.rk164 | DAL13 | 3 | 164 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945086 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 10 | -
dal13.sr03.rk165 | DAL13 | 3 | 165 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945088 | 0 | 4 | L4 | Z4-375 | 15 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 11 | dal13.sr03.rk155 - dal13.sr03.rk165
dal13.sr03.rk166 | DAL13 | 3 | 166 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945090 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr03.rk167 | DAL13 | 3 | 167 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945092 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk168 | DAL13 | 3 | 168 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945094 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk169 | DAL13 | 3 | 169 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945096 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk170 | DAL13 | 3 | 170 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945098 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk171 | DAL13 | 3 | 171 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945100 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk172 | DAL13 | 3 | 172 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945102 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk173 | DAL13 | 3 | 173 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945104 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 8 | -
dal13.sr03.rk174 | DAL13 | 3 | 174 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945106 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 9 | -
dal13.sr03.rk175 | DAL13 | 3 | 175 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945108 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 10 | -
dal13.sr03.rk176 | DAL13 | 3 | 176 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945110 | 0 | 4 | L4 | Z4-375 | 16 | vlam - 10/20/2022 - Setting to Unallocated-Planned. PowerVS moved to sr03.rk177-187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 11 | dal13.sr03.rk166 - dal13.sr03.rk176
dal13.sr03.rk177 | DAL13 | 3 | 177 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945112 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 50 | 0 | 0 | 22 | 22 | 0 | 50 | 28 | 28 | 50 | 0 | 0.236 | 2.5455 | 0 | PowerVS - Planned | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | S | 0 | -
dal13.sr03.rk178 | DAL13 | 3 | 178 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945114 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 50 | 0 | 0 | 22 | 22 | 0 | 50 | 28 | 28 | 50 | 0 | 0.236 | 2.5455 | 0 | PowerVS - Planned | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk179 | DAL13 | 3 | 179 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945116 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk180 | DAL13 | 3 | 180 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945118 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk181 | DAL13 | 3 | 181 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945120 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk182 | DAL13 | 3 | 182 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945122 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk183 | DAL13 | 3 | 183 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945124 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk184 | DAL13 | 3 | 184 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945126 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk185 | DAL13 | 3 | 185 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945128 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk186 | DAL13 | 3 | 186 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945130 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.236 | 4.5455 | 0 | PowerVS - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | - | 0 | -
dal13.sr03.rk187 | DAL13 | 3 | 187 | 3 | 10G | Dual Path | Sellable | PowerVS | PowerVS | Planned | 50 | 1945132 | 11.8 | 4 | L4 | Z4-375 | 17 | vlam - 10/20/2022 - Allocated to PowerVS per CAPREQ-749 |  | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 50 | 0 | 0 | 22 | 22 | 0 | 50 | 28 | 28 | 50 | 0 | 0.236 | 2.5455 | 0 | PowerVS - Planned | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11.8 | 0 | E | 0 | -
dal13.sr03.rk188 | DAL13 | 3 | 188 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945134 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.19 | 4.5455 | 0 | Network - Live | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | S | 1 | -
dal13.sr03.rk189 | DAL13 | 3 | 189 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945136 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 8 | 0 | 0 | 8 | 0 | 42 | 42 | 42 | 42 | 0 | 0.19 | 3.8182 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk190 | DAL13 | 3 | 190 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945138 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.19 | 4.5455 | 0 | Network - Live | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 1 | -
dal13.sr03.rk191 | DAL13 | 3 | 191 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945140 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 50 | 2 | 0 | 0 | 2 | 0 | 48 | 48 | 48 | 48 | 0 | 0.19 | 4.3636 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk192 | DAL13 | 3 | 192 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945142 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 4 | 9 | 0 | 0 | 0 | 0 | 4 | 9 | 50 | 17 | 0 | 0 | 17 | 0 | 33 | 33 | 33 | 33 | 0 | 0.19 | 3 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk193 | DAL13 | 3 | 193 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945144 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 50 | 23 | 0 | 0 | 23 | 0 | 27 | 27 | 27 | 27 | 0 | 0.19 | 2.4545 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk194 | DAL13 | 3 | 194 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945146 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.19 | 2.5455 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk195 | DAL13 | 3 | 195 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945148 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.19 | 2.5455 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk196 | DAL13 | 3 | 196 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945150 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.19 | 2.5455 | 0 | Network - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 0 | -
dal13.sr03.rk197 | DAL13 | 3 | 197 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945152 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.19 | 4.5455 | 0 | Network - Live | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 1 | -
dal13.sr03.rk198 | DAL13 | 3 | 198 | 3 | 10G | Dual Path | Unsellable | Network | Router | Live | 50 | 1945154 | 9.5 | 4 | L4 | Z4-375 | 18 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.19 | 4.5455 | 0 | Network - Live | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | - | 2 | -
dal13.sr03.rk199 | DAL13 | 3 | 199 | 3 | 10G | Dual Path | Unsellable | Network | Lab | Live | 50 | 1945156 | 9.5 | 4 | L4 | Z4-375 | 18 | acoleman - Direct Link Lab, requested through email - acoleman 9/22/21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.19 | 4.5455 | 0 | Network - Live | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 9.5 | 0 | E | 3 | -
dal13.sr03.rk200 | DAL13 | 3 | 200 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945158 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 18 | 0 | 0 | 18 | 0 | 32 | 32 | 32 | 32 | 0 | 0.064 | 2.9091 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | S | 0 | -
dal13.sr03.rk201 | DAL13 | 3 | 201 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945160 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 10 | 0 | 0 | 10 | 0 | 40 | 40 | 40 | 40 | 0 | 0.064 | 3.6364 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk202 | DAL13 | 3 | 202 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945162 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 1 | -
dal13.sr03.rk203 | DAL13 | 3 | 203 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945164 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 2 | -
dal13.sr03.rk204 | DAL13 | 3 | 204 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945166 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.064 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk205 | DAL13 | 3 | 205 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945168 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 2 | 50 | 1 | 1 | 0 | 2 | 0 | 49 | 48 | 49 | 49 | 0 | 0.064 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk206 | DAL13 | 3 | 206 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945170 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 16 | 0 | 0 | 16 | 0 | 34 | 34 | 34 | 34 | 0 | 0.064 | 3.0909 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk207 | DAL13 | 3 | 207 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945172 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 20 | 20 | 0 | 0.064 | 1.8182 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk208 | DAL13 | 3 | 208 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945174 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.064 | 2.5455 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk209 | DAL13 | 3 | 209 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945176 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 1 | -
dal13.sr03.rk210 | DAL13 | 3 | 210 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945178 | 3.2 | 4 | L4 | Z3-375 | 19 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | E | 2 | -
dal13.sr03.rk211 | DAL13 | 3 | 211 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945180 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 15 | 0 | 0 | 15 | 0 | 35 | 35 | 35 | 35 | 0 | 0.058 | 3.1818 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | S | 0 | -
dal13.sr03.rk212 | DAL13 | 3 | 212 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945182 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 7 | 0 | 0 | 7 | 0 | 43 | 43 | 43 | 43 | 0 | 0.058 | 3.9091 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | - | 0 | -
dal13.sr03.rk213 | DAL13 | 3 | 213 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945184 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.058 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9 | 0 | - | 1 | -
dal13.sr03.rk214 | DAL13 | 3 | 214 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945186 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.058 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9 | 0 | - | 2 | -
dal13.sr03.rk215 | DAL13 | 3 | 215 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945188 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 13 | 0 | 0 | 13 | 0 | 37 | 37 | 37 | 37 | 0 | 0.058 | 3.3636 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | - | 0 | -
dal13.sr03.rk216 | DAL13 | 3 | 216 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945190 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.058 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | - | 0 | -
dal13.sr03.rk217 | DAL13 | 3 | 217 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945192 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.058 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9 | 0 | - | 1 | -
dal13.sr03.rk218 | DAL13 | 3 | 218 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945194 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 20 | 20 | 0 | 0.058 | 1.8182 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | - | 0 | -
dal13.sr03.rk219 | DAL13 | 3 | 219 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945196 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 22 | 0 | 0 | 22 | 0 | 28 | 28 | 28 | 28 | 0 | 0.058 | 2.5455 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | - | 0 | -
dal13.sr03.rk220 | DAL13 | 3 | 220 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945198 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 16 | 0 | 0 | 16 | 0 | 34 | 34 | 34 | 34 | 0 | 0.058 | 3.0909 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 2.9 | 0 | - | 0 | -
dal13.sr03.rk221 | DAL13 | 3 | 221 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945200 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.058 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9 | 0 | - | 1 | -
dal13.sr03.rk222 | DAL13 | 3 | 222 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945202 | 2.9 | 4 | L4 | Z3-375 | 20 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.058 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9 | 0 | E | 2 | -
dal13.sr03.rk223 | DAL13 | 3 | 223 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945204 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | S | 1 | -
dal13.sr03.rk224 | DAL13 | 3 | 224 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945206 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 2 | -
dal13.sr03.rk225 | DAL13 | 3 | 225 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945208 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.064 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk226 | DAL13 | 3 | 226 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945210 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.064 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk227 | DAL13 | 3 | 227 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945212 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.064 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk228 | DAL13 | 3 | 228 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945214 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 49 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 1 | -
dal13.sr03.rk229 | DAL13 | 3 | 229 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945216 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 50 | 0 | 1 | 0 | 1 | 0 | 50 | 49 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 2 | -
dal13.sr03.rk230 | DAL13 | 3 | 230 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Live | 50 | 1945218 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.064 | 4.4545 | 0 | Storage - Live | N | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 3.2 | 0 | - | 0 | -
dal13.sr03.rk231 | DAL13 | 3 | 231 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945220 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 1 | -
dal13.sr03.rk232 | DAL13 | 3 | 232 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945222 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | - | 2 | -
dal13.sr03.rk233 | DAL13 | 3 | 233 | 3 | 10G | Dual Path | Sellable | Storage | File/Block | Planned | 50 | 1945224 | 3.2 | 4 | L4 | Z3-375 | 21 | vlam - vlam - 9/27/21 - This has been allocated for File/Block per CAPREQ-618. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.064 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.2 | 0 | E | 3 | -
dal13.sr03.rk234 | DAL13 | 3 | 234 | 3 | 10G | Dual Path | Sellable | Storage | COS | Planned | 50 | 1945226 | 14 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.28 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | S | 1 | -
dal13.sr03.rk235 | DAL13 | 3 | 235 | 3 | 10G | Dual Path | Sellable | Storage | COS | Planned | 50 | 1945228 | 14 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.28 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | - | 2 | -
dal13.sr03.rk236 | DAL13 | 3 | 236 | 3 | 10G | Dual Path | Sellable | Storage | COS | Planned | 50 | 1945230 | 14 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.28 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | - | 3 | -
dal13.sr03.rk237 | DAL13 | 3 | 237 | 3 | 10G | Dual Path | Sellable | Storage | COS | Planned | 50 | 1945232 | 14 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.28 | 4.5455 | 0 | Storage - Planned | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 0 | - | 4 | -
dal13.sr03.rk238 | DAL13 | 3 | 238 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945234 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk239 | DAL13 | 3 | 239 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945236 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk240 | DAL13 | 3 | 240 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945238 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk241 | DAL13 | 3 | 241 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945240 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 8 | -
dal13.sr03.rk242 | DAL13 | 3 | 242 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945242 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 9 | -
dal13.sr03.rk243 | DAL13 | 3 | 243 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945244 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 10 | -
dal13.sr03.rk244 | DAL13 | 3 | 244 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945246 | 0 | 4 | L4 | Z3-375 | 22 | vlam - 4/15/2024 - Will only need 4 rack NGDC design - will use racks 234-237 per CAPREQ-531. Power in the zone also limited, setting to Unallocated Power Limit. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 11 | dal13.sr03.rk234 - dal13.sr03.rk244
dal13.sr03.rk245 | DAL13 | 3 | 245 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Live | 50 | 3461176 | 15 | 4 | L4 | Z3-375 | 23 | vlam - 10/4/21 - updated for CAPREQ-625 per acoleman |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.3 | 0.81818 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | S | 0 | -
dal13.sr03.rk246 | DAL13 | 3 | 246 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Live | 50 | 3451908 | 15 | 4 | L4 | Z3-375 | 23 | sthornton - Set to Active per ticket https://internal.softlayer.com/Ticket/ticketEdit/154041394 |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.3 | 0.81818 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr03.rk247 | DAL13 | 3 | 247 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Live | 50 | 3448134 | 15 | 4 | L4 | Z3-375 | 23 | sthornton - Set to Active per ticket https://internal.softlayer.com/Ticket/ticketEdit/154041394 |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.3 | 0.81818 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 15 | 0 | - | 0 | -
dal13.sr03.rk248 | DAL13 | 3 | 248 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Live | 50 | 3464320 | 15 | 4 | L4 | Unknown | 23 | sthornton - Set to Active per ticket https://internal.softlayer.com/Ticket/ticketEdit/154041394 |  | 20 | 23 | 0 | 0 | 0 | 0 | 20 | 23 | 50 | 41 | 0 | 0 | 41 | 0 | 9 | 9 | 9 | 9 | 0 | 0.3 | 0.81818 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr03.rk249 | DAL13 | 3 | 249 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3533678 | 20 | 4 | L4 | Unknown | 27 | ysilva - 2/8/2024 - Allocated to NG Compute (QZ2) per DCL-3123 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr03.rk250 | DAL13 | 3 | 250 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945258 | 15 | 4 | L4 | Z3-375 | 23 | acoleman - acoleman - 10/4/21 - updated for CAPREQ-625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk251 | DAL13 | 3 | 251 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945260 | 15 | 4 | L4 | Z3-375 | 23 | acoleman - acoleman - 10/4/21 - updated for CAPREQ-625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk252 | DAL13 | 3 | 252 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945262 | 15 | 4 | L4 | Z3-375 | 23 | acoleman - acoleman - 10/4/21 - updated for CAPREQ-625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk253 | DAL13 | 3 | 253 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945264 | 15 | 4 | L4 | Z3-375 | 23 | acoleman - acoleman - 10/4/21 - updated for CAPREQ-625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk254 | DAL13 | 3 | 254 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945266 | 15 | 4 | L4 | Z3-375 | 23 | acoleman - acoleman - 10/4/21 - updated for CAPREQ-625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk255 | DAL13 | 3 | 255 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945268 | 15 | 4 | L4 | Z3-375 | 23 | acoleman - acoleman - 10/4/21 - updated for CAPREQ-625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | E | 0 | -
dal13.sr03.rk256 | DAL13 | 3 | 256 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945270 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | S | 1 | -
dal13.sr03.rk257 | DAL13 | 3 | 257 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945272 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk258 | DAL13 | 3 | 258 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945274 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk259 | DAL13 | 3 | 259 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945276 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk260 | DAL13 | 3 | 260 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945278 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk261 | DAL13 | 3 | 261 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945280 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk262 | DAL13 | 3 | 262 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945282 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk263 | DAL13 | 3 | 263 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945284 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 8 | -
dal13.sr03.rk264 | DAL13 | 3 | 264 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945286 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 9 | -
dal13.sr03.rk265 | DAL13 | 3 | 265 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945288 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 10 | -
dal13.sr03.rk266 | DAL13 | 3 | 266 | 3 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945290 | 0 | 4 | L4 | Z3-375 | 24 | ccoronado - Updating SL tag per Sean Adams. Ticket: 138819034 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 11 | dal13.sr03.rk256 - dal13.sr03.rk266
dal13.sr03.rk267 | DAL13 | 3 | 267 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3489975 | 20 | 4 | L4 | Z2-375 | 25 | ccoronado - Adding SL tag per Phillip Huffman. Ticket: 154474399 |  | 21 | 24 | 0 | 0 | 0 | 0 | 21 | 24 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | S | 0 | -
dal13.sr03.rk268 | DAL13 | 3 | 268 | G1 | 10G | Dual Path | Sellable | NGDC | Bare Metal | Planned | 50 | 3541152 | 20 | 4 | L4 | Z2-375 | 25 | vlam - 2/8/2024 - Allocated to NGDC Integration - Bare Metal per DCL-3239 |  | 0 | 0 | 4 | 0 | 4 | 0 | 0 | 4 | 50 | 0 | 6 | 0 | 6 | 0 | 50 | 44 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk269 | DAL13 | 3 | 269 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 1945296 | 20 | 4 | L4 | Z2-375 | 25 | vlam - 2/8/2024 - Allocated to NGDC Integration Compute per DCL-3339 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk270 | DAL13 | 3 | 270 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945298 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk271 | DAL13 | 3 | 271 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945300 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk272 | DAL13 | 3 | 272 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945302 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk273 | DAL13 | 3 | 273 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945304 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk274 | DAL13 | 3 | 274 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945306 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk275 | DAL13 | 3 | 275 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945308 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk276 | DAL13 | 3 | 276 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945310 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk277 | DAL13 | 3 | 277 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945312 | 0 | 4 | L4 | Z2-375 | 25 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk278 | DAL13 | 3 | 278 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3466274 | 20 | 4 | L4 | Unknown | 26 | ysilva - 2/15/2022 - This has been allocated for NG per CAPREQ-703 |  | 20 | 24 | 0 | 0 | 0 | 1 | 21 | 25 | 50 | 46 | 0 | 2 | 48 | 0 | 4 | 2 | 2 | 4 | 0 | 0.4 | 0.18182 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr03.rk279 | DAL13 | 3 | 279 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945316 | 15 | 4 | L4 | Z2-375 | 26 | vlam - 5/15/2024 - Acadia: VPC Block for VSI profile for BaaS - Development Infrastructure per DCL-3079 and VPCCDM-1751 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk280 | DAL13 | 3 | 280 | G1 | 10G | Dual Path | Sellable | Gen2 | Acadia | Planned | 50 | 1945318 | 15 | 4 | L4 | Z2-375 | 26 | vlam - 5/15/2024 - Acadia: VPC Block for VSI profile for BaaS - Development Infrastructure per DCL-3079 and VPCCDM-1751 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk281 | DAL13 | 3 | 281 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945320 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk282 | DAL13 | 3 | 282 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945322 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk283 | DAL13 | 3 | 283 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945324 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk284 | DAL13 | 3 | 284 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945326 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk285 | DAL13 | 3 | 285 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945328 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk286 | DAL13 | 3 | 286 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945330 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk287 | DAL13 | 3 | 287 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945332 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk288 | DAL13 | 3 | 288 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945334 | 0 | 4 | L4 | Z2-375 | 26 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk289 | DAL13 | 3 | 289 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3465050 | 20 | 4 | L4 | Unknown | 27 | ysilva - 2/15/2022 - This has been allocated for NG per CAPREQ-703 |  | 8 | 11 | 5 | 0 | 5 | 0 | 13 | 16 | 50 | 21 | 10 | 0 | 31 | 0 | 29 | 19 | 29 | 29 | 0 | 0.4 | 2.6364 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr03.rk290 | DAL13 | 3 | 290 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3465052 | 20 | 4 | L4 | Unknown | 27 | ysilva - 2/15/2022 - This has been allocated for NG per CAPREQ-703 |  | 8 | 11 | 7 | 0 | 7 | 0 | 15 | 18 | 50 | 21 | 14 | 0 | 35 | 0 | 29 | 15 | 29 | 29 | 0 | 0.4 | 2.6364 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr03.rk291 | DAL13 | 3 | 291 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 0 | 3465054 | 20 | 4 | L4 | Unknown | 27 | ysilva - 2/15/2022 - This has been allocated for NG per CAPREQ-703 |  | 9 | 13 | 9 | 0 | 9 | 0 | 18 | 22 | 50 | 24 | 18 | 0 | 42 | 0 | 26 | 8 | 26 | 26 | 0 | 0.4 | 2.3636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr03.rk292 | DAL13 | 3 | 292 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945342 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk293 | DAL13 | 3 | 293 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945344 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk294 | DAL13 | 3 | 294 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945346 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk295 | DAL13 | 3 | 295 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945348 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk296 | DAL13 | 3 | 296 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945350 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk297 | DAL13 | 3 | 297 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945352 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk298 | DAL13 | 3 | 298 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945354 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk299 | DAL13 | 3 | 299 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945356 | 0 | 4 | L4 | Z2-375 | 27 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk300 | DAL13 | 3 | 300 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3502561 | 20 | 4 | L4 | Z2-375 | 28 | hphan - Received order from dal07 per shipment ID 1067007 |  | 21 | 24 | 0 | 0 | 0 | 0 | 21 | 24 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr03.rk301 | DAL13 | 3 | 301 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3505959 | 20 | 4 | L4 | Z2-375 | 28 | ysilva - vlam - 9/28/2022 - Allocated to NG for Nov-Citi and SPR Beta per DCL-3212 |  | 21 | 24 | 0 | 0 | 0 | 0 | 21 | 24 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr03.rk302 | DAL13 | 3 | 302 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3505961 | 20 | 4 | L4 | Z2-375 | 28 | ysilva - vlam - 9/28/2022 - Allocated to NG for Nov-Citi and SPR Beta per DCL-3212 |  | 21 | 24 | 0 | 0 | 0 | 0 | 21 | 24 | 50 | 47 | 0 | 0 | 47 | 0 | 3 | 3 | 3 | 3 | 0 | 0.4 | 0.27273 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 20 | 0 | - | 0 | -
dal13.sr03.rk303 | DAL13 | 3 | 303 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945364 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk304 | DAL13 | 3 | 304 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945366 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk305 | DAL13 | 3 | 305 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945368 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk306 | DAL13 | 3 | 306 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945370 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk307 | DAL13 | 3 | 307 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945372 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk308 | DAL13 | 3 | 308 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945374 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk309 | DAL13 | 3 | 309 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945376 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk310 | DAL13 | 3 | 310 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945378 | 0 | 4 | L4 | Z2-375 | 28 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk311 | DAL13 | 3 | 311 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945380 | 20 | 4 | L4 | Z2-375 | 29 | vlam - 3/25/2024 - Allocated to NG for NG2 - BAU per DCL-3212 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | S | 0 | -
dal13.sr03.rk312 | DAL13 | 3 | 312 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945382 | 20 | 4 | L4 | Z2-375 | 29 | vlam - 3/25/2024 - Allocated to NG for NG2 - BAU per DCL-3212 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk313 | DAL13 | 3 | 313 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945384 | 20 | 4 | L4 | Z2-375 | 29 | vlam - 3/25/2024 - Allocated to NG for NG2 - BAU per DCL-3212 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk314 | DAL13 | 3 | 314 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945386 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk315 | DAL13 | 3 | 315 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945388 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk316 | DAL13 | 3 | 316 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945390 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk317 | DAL13 | 3 | 317 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945392 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk318 | DAL13 | 3 | 318 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945394 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk319 | DAL13 | 3 | 319 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945396 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk320 | DAL13 | 3 | 320 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945398 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk321 | DAL13 | 3 | 321 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945400 | 0 | 4 | L4 | Z2-375 | 29 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk322 | DAL13 | 3 | 322 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3503543 | 20 | 4 | L4 | Unknown | 30 | hphan - Received order from dal07 per shipment ID 1067007 |  | 22 | 22 | 3 | 0 | 3 | 0 | 22 | 25 | 50 | 44 | 5 | 0 | 49 | 0 | 6 | 1 | 6 | 6 | 0 | 0.4 | 0.54545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr03.rk323 | DAL13 | 3 | 323 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3503545 | 20 | 4 | L4 | Unknown | 30 | hphan - Received order from dal07 per shipment ID 1067007 |  | 22 | 22 | 3 | 0 | 3 | 0 | 22 | 25 | 50 | 44 | 5 | 0 | 49 | 0 | 6 | 1 | 6 | 6 | 0 | 0.4 | 0.54545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr03.rk324 | DAL13 | 3 | 324 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3503547 | 20 | 4 | L4 | Unknown | 30 | hphan - Received order from dal07 per shipment ID 1067007 |  | 22 | 22 | 3 | 0 | 3 | 0 | 22 | 25 | 50 | 44 | 5 | 0 | 49 | 0 | 6 | 1 | 6 | 6 | 0 | 0.4 | 0.54545 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr03.rk325 | DAL13 | 3 | 325 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945408 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk326 | DAL13 | 3 | 326 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945410 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk327 | DAL13 | 3 | 327 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945412 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk328 | DAL13 | 3 | 328 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945414 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk329 | DAL13 | 3 | 329 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945416 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk330 | DAL13 | 3 | 330 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945418 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk331 | DAL13 | 3 | 331 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945420 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk332 | DAL13 | 3 | 332 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945422 | 0 | 4 | L4 | Z2-375 | 30 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk333 | DAL13 | 3 | 333 | G1 | 10G | Dual Path | Unsellable | Network | Fiber | Planned | 50 | 1945424 | 0 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0 | 4.5455 | 0 | Network - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | S | 1 | -
dal13.sr03.rk334 | DAL13 | 3 | 334 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1945426 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 5 | 50 | 0 | 17 | 0 | 17 | 0 | 50 | 33 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk335 | DAL13 | 3 | 335 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1945428 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 50 | 0 | 26 | 0 | 26 | 0 | 50 | 24 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk336 | DAL13 | 3 | 336 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1945430 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 50 | 0 | 26 | 0 | 26 | 0 | 50 | 24 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk337 | DAL13 | 3 | 337 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Live | 50 | 1945432 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 1 | 0 | 0 | 1 | 0 | 49 | 49 | 49 | 49 | 0 | 0.3 | 4.4545 | 0 | NGDC - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr03.rk338 | DAL13 | 3 | 338 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1945434 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 3 | 0 | 3 | 1 | 0 | 4 | 50 | 0 | 9 | 3 | 12 | 0 | 50 | 38 | 47 | 50 | 0 | 0.3 | 4.2727 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk339 | DAL13 | 3 | 339 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Live | 50 | 1945436 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 4 | 6 | 0 | 6 | 0 | 0 | 10 | 50 | 6 | 6 | 0 | 12 | 0 | 44 | 38 | 44 | 44 | 0 | 0.3 | 4 | 0 | NGDC - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr03.rk340 | DAL13 | 3 | 340 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Live | 50 | 1945438 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 4 | 6 | 6 | 0 | 6 | 0 | 4 | 12 | 50 | 10 | 8 | 0 | 18 | 0 | 40 | 32 | 40 | 40 | 0 | 0.3 | 3.6364 | 0 | NGDC - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr03.rk341 | DAL13 | 3 | 341 | G1 | 10G | Dual Path | Unsellable | NGDC | Network | Planned | 50 | 1945440 | 15 | 4 | L4 | Z1-375 | 31 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk342 | DAL13 | 3 | 342 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945442 | 0 | 4 | L4 | Z1-375 | 31 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk343 | DAL13 | 3 | 343 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945444 | 0 | 4 | L4 | Z1-375 | 31 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 2 | -
dal13.sr03.rk344 | DAL13 | 3 | 344 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1945446 | 15 | 4 | L4 | Z1-375 | 32 | vlam - 2/15/2022 - This has been allocated for NG AGG and MAGG per DCL-3079 |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 3 | 0 | 0 | 3 | 0 | 47 | 47 | 47 | 47 | 0 | 0.3 | 4.2727 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | S | 0 | -
dal13.sr03.rk345 | DAL13 | 3 | 345 | G1 | 10G | Dual Path | Unsellable | Gen2 | Network | Live | 50 | 1945448 | 15 | 4 | L4 | Z1-375 | 32 | vlam - 2/15/2022 - This has been allocated for NG AGG and MAGG per DCL-3079 |  | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 4 | 50 | 2 | 2 | 0 | 4 | 0 | 48 | 46 | 48 | 48 | 0 | 0.3 | 4.3636 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 15 | 0 | - | 0 | -
dal13.sr03.rk346 | DAL13 | 3 | 346 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945450 | 20 | 4 | L4 | Z1-375 | 32 | vlam - vlam - 2/15/2022 - This has been allocated for NG per CAPREQ-704 |  | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 3 | 50 | 0 | 5 | 0 | 5 | 0 | 50 | 45 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk347 | DAL13 | 3 | 347 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945452 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk348 | DAL13 | 3 | 348 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945454 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk349 | DAL13 | 3 | 349 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945456 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk350 | DAL13 | 3 | 350 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945458 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk351 | DAL13 | 3 | 351 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945460 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk352 | DAL13 | 3 | 352 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945462 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk353 | DAL13 | 3 | 353 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945464 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk354 | DAL13 | 3 | 354 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945466 | 0 | 4 | L4 | Z1-375 | 32 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk355 | DAL13 | 3 | 355 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 3540538 | 15 | 4 | L4 | Z1-375 | 33 | ysilva - vlam - 03/23/23 - FedRAMP Integration and Staging. |  | 0 | 0 | 19 | 0 | 19 | 0 | 14 | 19 | 50 | 0 | 36 | 0 | 36 | 0 | 50 | 14 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | S | 0 | -
dal13.sr03.rk356 | DAL13 | 3 | 356 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 3540224 | 15 | 4 | L4 | Z1-375 | 33 | vlam - 3/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 17 | 0 | 17 | 0 | 12 | 17 | 50 | 0 | 32 | 0 | 32 | 0 | 50 | 18 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk357 | DAL13 | 3 | 357 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 3540226 | 15 | 4 | L4 | Z1-375 | 33 | vlam - 3/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 17 | 0 | 17 | 0 | 12 | 17 | 50 | 0 | 32 | 0 | 32 | 0 | 50 | 18 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk358 | DAL13 | 3 | 358 | G1 | 10G | Dual Path | Unsellable | NGDC | Management | Planned | 50 | 3540228 | 15 | 4 | L4 | Z1-375 | 33 | vlam - 3/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 19 | 0 | 19 | 0 | 14 | 19 | 50 | 0 | 36 | 0 | 36 | 0 | 50 | 14 | 50 | 50 | 0 | 0.3 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 0 | - | 0 | -
dal13.sr03.rk359 | DAL13 | 3 | 359 | G1 | 10G | Dual Path | Sellable | NGDC | File/Block | Planned | 50 | 1945476 | 6 | 4 | L4 | Z1-375 | 33 | vlam - 8/7/2023 - Allocated to FedRAMP Integration - File/Block per DCL-3079 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | - | 0 | -
dal13.sr03.rk360 | DAL13 | 3 | 360 | G1 | 10G | Dual Path | Sellable | NGDC | File/Block | Planned | 50 | 1945478 | 6 | 4 | L4 | Z1-375 | 33 | vlam - 8/7/2023 - Allocated to FedRAMP Integration - File/Block per DCL-3079 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.12 | 4.5455 | 0 | NGDC - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | - | 0 | -
dal13.sr03.rk361 | DAL13 | 3 | 361 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945480 | 0 | 4 | L4 | Z1-375 | 33 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk362 | DAL13 | 3 | 362 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945482 | 0 | 4 | L4 | Z1-375 | 33 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk363 | DAL13 | 3 | 363 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945484 | 0 | 4 | L4 | Z1-375 | 33 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk364 | DAL13 | 3 | 364 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945486 | 0 | 4 | L4 | Z1-375 | 33 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk365 | DAL13 | 3 | 365 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945488 | 0 | 4 | L4 | Z1-375 | 33 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 5 | -
dal13.sr03.rk366 | DAL13 | 3 | 366 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 3541154 | 20 | 4 | L4 | Z1-375 | 34 | vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 25 | 0 | 25 | 0 | 21 | 25 | 50 | 0 | 48 | 0 | 48 | 0 | 50 | 2 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | S | 0 | -
dal13.sr03.rk367 | DAL13 | 3 | 367 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 3541330 | 20 | 4 | L4 | Z1-375 | 34 | vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 18 | 0 | 18 | 0 | 13 | 18 | 50 | 0 | 34 | 0 | 34 | 0 | 50 | 16 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk368 | DAL13 | 3 | 368 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 3541332 | 20 | 4 | L4 | Z1-375 | 34 | vlam - 03/23/23 - FedRAMP Integration and Staging |  | 0 | 0 | 18 | 0 | 18 | 0 | 13 | 18 | 50 | 0 | 34 | 0 | 34 | 0 | 50 | 16 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk369 | DAL13 | 3 | 369 | G1 | 10G | Dual Path | Sellable | NGDC | Compute | Planned | 50 | 1945496 | 20 | 4 | L4 | Z1-375 | 34 | vlam - 2/8/2024 - Allocated to NGDC Integration Compute per DCL-3339 |  | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 50 | 0 | 2 | 0 | 2 | 0 | 50 | 48 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | NGDC - Planned | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk370 | DAL13 | 3 | 370 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945498 | 0 | 4 | L4 | Z1-375 | 34 | vlam - 2/8/2024 - No longer needed for Z Mainframe. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk371 | DAL13 | 3 | 371 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945500 | 0 | 4 | L4 | Z1-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk372 | DAL13 | 3 | 372 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945502 | 0 | 4 | L4 | Z1-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk373 | DAL13 | 3 | 373 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945504 | 0 | 4 | L4 | Z1-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk374 | DAL13 | 3 | 374 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945506 | 0 | 4 | L4 | Z1-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk375 | DAL13 | 3 | 375 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945508 | 0 | 4 | L4 | Z1-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk376 | DAL13 | 3 | 376 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945510 | 0 | 4 | L4 | Z1-375 | 34 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 7 | -
dal13.sr03.rk377 | DAL13 | 3 | 377 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3495913 | 20 | 4 | L4 | Z1-375 | 35 | ccoronado - Adding SL tag per Anthony Neis. Ticket:154734671 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr03.rk378 | DAL13 | 3 | 378 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3495915 | 20 | 4 | L4 | Z1-375 | 35 | ccoronado - Adding SL tag per Anthony Neis. Ticket:154734671 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr03.rk379 | DAL13 | 3 | 379 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3495917 | 20 | 4 | L4 | Z1-375 | 35 | ccoronado - Adding SL tag per Anthony Neis. Ticket:154734671 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | - | 0 | -
dal13.sr03.rk380 | DAL13 | 3 | 380 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945518 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk381 | DAL13 | 3 | 381 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945520 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk382 | DAL13 | 3 | 382 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945522 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk383 | DAL13 | 3 | 383 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945524 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk384 | DAL13 | 3 | 384 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945526 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk385 | DAL13 | 3 | 385 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945528 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk386 | DAL13 | 3 | 386 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945530 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk387 | DAL13 | 3 | 387 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945532 | 0 | 4 | L4 | Z1-375 | 35 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -
dal13.sr03.rk388 | DAL13 | 3 | 388 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Live | 50 | 3495919 | 20 | 4 | L4 | Z1-375 | 36 | vlam - 4/5/2024 - Allocated to NG for Flex per DCL-3309 |  | 22 | 25 | 0 | 0 | 0 | 0 | 22 | 25 | 50 | 49 | 0 | 0 | 49 | 0 | 1 | 1 | 1 | 1 | 0 | 0.4 | 0.090909 | 0 | Gen2 - Live | N | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO IP | 20 | 0 | S | 0 | -
dal13.sr03.rk389 | DAL13 | 3 | 389 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945536 | 20 | 4 | L4 | Z1-375 | 36 | vlam - 8/1/2022 - Allocated for NG Dell GPU Refresh per DCL-3309 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk390 | DAL13 | 3 | 390 | G1 | 10G | Dual Path | Sellable | Gen2 | Compute | Planned | 50 | 1945538 | 20 | 4 | L4 | Z1-375 | 36 | vlam - 8/1/2022 - Allocated for NG Dell GPU Refresh per DCL-3309 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 0.4 | 4.5455 | 0 | Gen2 - Planned | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | - | 0 | -
dal13.sr03.rk391 | DAL13 | 3 | 391 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945540 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 1 | -
dal13.sr03.rk392 | DAL13 | 3 | 392 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945542 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 2 | -
dal13.sr03.rk393 | DAL13 | 3 | 393 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945544 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 3 | -
dal13.sr03.rk394 | DAL13 | 3 | 394 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945546 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 4 | -
dal13.sr03.rk395 | DAL13 | 3 | 395 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945548 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 5 | -
dal13.sr03.rk396 | DAL13 | 3 | 396 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945550 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 6 | -
dal13.sr03.rk397 | DAL13 | 3 | 397 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945552 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | - | 7 | -
dal13.sr03.rk398 | DAL13 | 3 | 398 | G1 | 10G | Dual Path | Sellable | Unallocated | Unallocated | Power Limit | 50 | 1945554 | 0 | 4 | L4 | Z1-375 | 36 | astelmach - 8/2/23 - This power limit rack has been updated from Gen2/Compute to Unallocated/Unallocated. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 0 | 4.5455 | 0 | Unallocated - Power Limit | Y | DAL13-10G1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO PS READING | 0 | 0 | E | 8 | -

## power_data
DC | SR | Rack Path | PS Type | PS1 L1 | PS1 L2 | PS1 L3 | PS2 L1 | PS2 L2 | PS2 L3 | PS3 L1 | PS3 L2 | PS3 L3 | PS4 L1 | PS4 L2 | PS4 L3 | Avg. Amps | Total kW | Type | Sub-Type | Status | kW/Rack | Zone-Power | Utilization | IMS Reading | Rack Reading
DAL13 | 1 | dal13.sr01.rk01 | Dual Redundancy-3Phase | 96 | 18 | 33 | 96 | 29 | 33 | 100 | 23 | 84 | 70 | 31 | 22 | 5.2917 | 3.4828 | Compute | Hybrid | Live | 10 | Z1-375 | 0.34828 | 8.281 | 8.281
DAL13 | 1 | dal13.sr01.rk02 | Redundant-3Phase | 96 | 23 | 32 | 96 | 22 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 3.2579 | Compute | Hybrid | Live | 10 | Z1-375 | 0.32579 | 9.194 | 9.194
DAL13 | 1 | dal13.sr01.rk03 | Redundant-Single | 82 | 3.1 | 3.1 | 81 | 3.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 8.15 | 6.194 | Compute | Hybrid | Live | 10 | Z1-375 | 0.6194 | 7.548 | 7.548
DAL13 | 1 | dal13.sr01.rk04 | Dual Redundancy-Single | 81 | 0 | 0 | 84 | 0 | 0 | 23 | 0 | 0 | 42 | 0 | 0 | 5.75 | 8.74 | Compute | Hybrid | Live | 10 | Z1-375 | 0.874 | 8.958 | 8.958
DAL13 | 1 | dal13.sr01.rk05 | Dual Redundancy-3Phase | 82 | 22 | 51 | 81 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 3.4224 | Compute | Hybrid | Live | 10 | Z1-375 | 0.34224 | 8.914 | 8.914
DAL13 | 1 | dal13.sr01.rk06 | Single-Single | 222 | 252 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 8.436 | Network | Aggregate | Live | 5 | Z1-375 | 1.6872 | 0 | 8.436
DAL13 | 1 | dal13.sr01.rk07 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z1-375 | 0 | 8.005 | 8.005
DAL13 | 1 | dal13.sr01.rk08 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z1-375 | 0 | 8.993 | 8.993
DAL13 | 1 | dal13.sr01.rk09 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z1-375 | 0 | 9.215 | 9.215
DAL13 | 1 | dal13.sr01.rk10 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z1-375 | 0 | 10.059 | 10.059
DAL13 | 1 | dal13.sr01.rk11 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z1-375 | 0 | 9.162 | 9.162
DAL13 | 1 | dal13.sr01.rk12 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 3.96 | 3.96
DAL13 | 1 | dal13.sr01.rk13 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.671 | 5.671
DAL13 | 1 | dal13.sr01.rk14 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.221 | 4.221
DAL13 | 1 | dal13.sr01.rk15 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.326 | 5.326
DAL13 | 1 | dal13.sr01.rk16 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.369 | 5.369
DAL13 | 1 | dal13.sr01.rk17 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk18 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.073 | 6.073
DAL13 | 1 | dal13.sr01.rk19 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 3.188 | 3.188
DAL13 | 1 | dal13.sr01.rk20 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.321 | 4.321
DAL13 | 1 | dal13.sr01.rk21 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 3.875 | 3.875
DAL13 | 1 | dal13.sr01.rk22 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | COD | Live | 6 | Z1-375 | 0 | 1.437 | 1.437
DAL13 | 1 | dal13.sr01.rk23 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.24 | 5.24
DAL13 | 1 | dal13.sr01.rk24 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.351 | 6.351
DAL13 | 1 | dal13.sr01.rk25 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.707 | 6.707
DAL13 | 1 | dal13.sr01.rk26 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.046 | 6.046
DAL13 | 1 | dal13.sr01.rk27 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.35 | 6.35
DAL13 | 1 | dal13.sr01.rk28 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk29 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.949 | 5.949
DAL13 | 1 | dal13.sr01.rk30 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 7.789 | 7.789
DAL13 | 1 | dal13.sr01.rk31 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 7.741 | 7.741
DAL13 | 1 | dal13.sr01.rk32 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 7.184 | 7.184
DAL13 | 1 | dal13.sr01.rk33 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.433 | 6.433
DAL13 | 1 | dal13.sr01.rk34 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.21 | 5.21
DAL13 | 1 | dal13.sr01.rk35 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.349 | 4.349
DAL13 | 1 | dal13.sr01.rk36 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.399 | 5.399
DAL13 | 1 | dal13.sr01.rk37 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 3.894 | 3.894
DAL13 | 1 | dal13.sr01.rk38 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.331 | 4.331
DAL13 | 1 | dal13.sr01.rk39 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk40 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.299 | 4.299
DAL13 | 1 | dal13.sr01.rk41 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.957 | 5.957
DAL13 | 1 | dal13.sr01.rk42 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 3.214 | 3.214
DAL13 | 1 | dal13.sr01.rk43 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.008 | 4.008
DAL13 | 1 | dal13.sr01.rk44 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.983 | 4.983
DAL13 | 1 | dal13.sr01.rk45 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.315 | 3.315
DAL13 | 1 | dal13.sr01.rk46 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.318 | 4.318
DAL13 | 1 | dal13.sr01.rk47 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.21 | 4.21
DAL13 | 1 | dal13.sr01.rk48 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 2.805 | 2.805
DAL13 | 1 | dal13.sr01.rk49 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.775 | 3.775
DAL13 | 1 | dal13.sr01.rk50 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk51 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 2.85 | 2.85
DAL13 | 1 | dal13.sr01.rk52 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 2.928 | 2.928
DAL13 | 1 | dal13.sr01.rk53 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.102 | 3.102
DAL13 | 1 | dal13.sr01.rk54 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.627 | 3.627
DAL13 | 1 | dal13.sr01.rk55 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.286 | 3.286
DAL13 | 1 | dal13.sr01.rk56 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.638 | 4.638
DAL13 | 1 | dal13.sr01.rk57 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.324 | 4.324
DAL13 | 1 | dal13.sr01.rk58 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.353 | 4.353
DAL13 | 1 | dal13.sr01.rk59 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 6.184 | 6.184
DAL13 | 1 | dal13.sr01.rk60 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.964 | 4.964
DAL13 | 1 | dal13.sr01.rk61 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk62 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.363 | 4.363
DAL13 | 1 | dal13.sr01.rk63 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.675 | 3.675
DAL13 | 1 | dal13.sr01.rk64 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.632 | 4.632
DAL13 | 1 | dal13.sr01.rk65 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.078 | 3.078
DAL13 | 1 | dal13.sr01.rk66 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 7.439 | 7.439
DAL13 | 1 | dal13.sr01.rk67 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 3.397 | 3.397
DAL13 | 1 | dal13.sr01.rk68 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 6.119 | 6.119
DAL13 | 1 | dal13.sr01.rk69 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 7.987 | 7.987
DAL13 | 1 | dal13.sr01.rk70 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 7.014 | 7.014
DAL13 | 1 | dal13.sr01.rk71 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 3.642 | 3.642
DAL13 | 1 | dal13.sr01.rk72 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk73 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 3.756 | 3.756
DAL13 | 1 | dal13.sr01.rk74 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 4.568 | 4.568
DAL13 | 1 | dal13.sr01.rk75 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 4.748 | 4.748
DAL13 | 1 | dal13.sr01.rk76 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 6.303 | 6.303
DAL13 | 1 | dal13.sr01.rk77 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0 | 8.328 | 8.328
DAL13 | 1 | dal13.sr01.rk78 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.45 | 4.45
DAL13 | 1 | dal13.sr01.rk79 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.856 | 4.856
DAL13 | 1 | dal13.sr01.rk80 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.779 | 3.779
DAL13 | 1 | dal13.sr01.rk81 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.872 | 3.872
DAL13 | 1 | dal13.sr01.rk82 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.468 | 3.468
DAL13 | 1 | dal13.sr01.rk83 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk84 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.209 | 5.209
DAL13 | 1 | dal13.sr01.rk85 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 6.207 | 6.207
DAL13 | 1 | dal13.sr01.rk86 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 8.965 | 8.965
DAL13 | 1 | dal13.sr01.rk87 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.467 | 5.467
DAL13 | 1 | dal13.sr01.rk88 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 7.852 | 7.852
DAL13 | 1 | dal13.sr01.rk89 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk90 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk91 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk92 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk93 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk94 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk95 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk96 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk97 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk98 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk99 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk100 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk101 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk102 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk103 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk104 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk105 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk106 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk107 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk108 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk109 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk110 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk111 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk112 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk113 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk114 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk115 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk116 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk117 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk118 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk119 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk120 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk121 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk122 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk123 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk124 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk125 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk126 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk127 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk128 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk129 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk130 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk131 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk132 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk133 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk134 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk135 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk136 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk137 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk138 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk139 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk140 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk141 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk142 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk143 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk144 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | DTS | Live | 4.6 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk145 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk146 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk147 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk148 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk149 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk150 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk151 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk152 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk153 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk154 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk155 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk156 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Fiber | Live | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk157 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk158 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk159 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk160 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk161 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk162 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk163 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk164 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk165 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk166 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk167 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.1 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk168 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk169 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk170 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk171 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk172 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk173 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Network Spares | Live | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk174 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk175 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fabric | Server | Live | 4.6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk176 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Load Balancer | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk177 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Firewall | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk178 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Firewall | Live | 6 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk179 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 7.764 | 7.764
DAL13 | 1 | dal13.sr01.rk180 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 7.775 | 7.775
DAL13 | 1 | dal13.sr01.rk181 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.065 | 10.065
DAL13 | 1 | dal13.sr01.rk182 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 9.512 | 9.512
DAL13 | 1 | dal13.sr01.rk183 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 9.06 | 9.06
DAL13 | 1 | dal13.sr01.rk184 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk185 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 9.843 | 9.843
DAL13 | 1 | dal13.sr01.rk186 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 5.258 | 5.258
DAL13 | 1 | dal13.sr01.rk187 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 8.45 | 8.45
DAL13 | 1 | dal13.sr01.rk188 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 11.057 | 11.057
DAL13 | 1 | dal13.sr01.rk189 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.207 | 10.207
DAL13 | 1 | dal13.sr01.rk190 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 2.478 | 2.478
DAL13 | 1 | dal13.sr01.rk191 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 3.406 | 3.406
DAL13 | 1 | dal13.sr01.rk192 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 2.324 | 2.324
DAL13 | 1 | dal13.sr01.rk193 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 3.026 | 3.026
DAL13 | 1 | dal13.sr01.rk194 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 3.978 | 3.978
DAL13 | 1 | dal13.sr01.rk195 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk196 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.459 | 4.459
DAL13 | 1 | dal13.sr01.rk197 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.419 | 5.419
DAL13 | 1 | dal13.sr01.rk198 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.604 | 5.604
DAL13 | 1 | dal13.sr01.rk199 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 3.918 | 3.918
DAL13 | 1 | dal13.sr01.rk200 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.838 | 5.838
DAL13 | 1 | dal13.sr01.rk201 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Ded. Firewall | Live | 6 | Z6-375 | 0 | 4.221 | 4.221
DAL13 | 1 | dal13.sr01.rk202 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.837 | 5.837
DAL13 | 1 | dal13.sr01.rk203 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 7.513 | 7.513
DAL13 | 1 | dal13.sr01.rk204 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.541 | 4.541
DAL13 | 1 | dal13.sr01.rk205 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.692 | 4.692
DAL13 | 1 | dal13.sr01.rk206 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk207 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.467 | 4.467
DAL13 | 1 | dal13.sr01.rk208 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 6.724 | 6.724
DAL13 | 1 | dal13.sr01.rk209 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.064 | 4.064
DAL13 | 1 | dal13.sr01.rk210 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 3.977 | 3.977
DAL13 | 1 | dal13.sr01.rk211 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 3.586 | 3.586
DAL13 | 1 | dal13.sr01.rk212 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 2.844 | 2.844
DAL13 | 1 | dal13.sr01.rk213 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.049 | 4.049
DAL13 | 1 | dal13.sr01.rk214 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 3.891 | 3.891
DAL13 | 1 | dal13.sr01.rk215 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.872 | 4.872
DAL13 | 1 | dal13.sr01.rk216 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.014 | 4.014
DAL13 | 1 | dal13.sr01.rk217 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk218 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.226 | 4.226
DAL13 | 1 | dal13.sr01.rk219 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 3.232 | 3.232
DAL13 | 1 | dal13.sr01.rk220 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.671 | 4.671
DAL13 | 1 | dal13.sr01.rk221 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.994 | 5.994
DAL13 | 1 | dal13.sr01.rk222 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 4.715 | 4.715
DAL13 | 1 | dal13.sr01.rk223 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.364 | 5.364
DAL13 | 1 | dal13.sr01.rk224 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.11 | 2.11
DAL13 | 1 | dal13.sr01.rk225 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.172 | 3.172
DAL13 | 1 | dal13.sr01.rk226 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.008 | 4.008
DAL13 | 1 | dal13.sr01.rk227 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.761 | 5.761
DAL13 | 1 | dal13.sr01.rk228 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk229 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.749 | 3.749
DAL13 | 1 | dal13.sr01.rk230 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 9.413 | 9.413
DAL13 | 1 | dal13.sr01.rk231 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 9.215 | 9.215
DAL13 | 1 | dal13.sr01.rk232 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.663 | 4.663
DAL13 | 1 | dal13.sr01.rk233 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.999 | 4.999
DAL13 | 1 | dal13.sr01.rk234 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk235 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk236 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk237 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk238 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk239 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk240 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk241 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk242 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk243 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk244 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk245 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.26 | 5.26
DAL13 | 1 | dal13.sr01.rk246 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.115 | 4.115
DAL13 | 1 | dal13.sr01.rk247 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.517 | 4.517
DAL13 | 1 | dal13.sr01.rk248 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.9 | 7.9
DAL13 | 1 | dal13.sr01.rk249 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.915 | 6.915
DAL13 | 1 | dal13.sr01.rk250 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk251 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 9.027 | 9.027
DAL13 | 1 | dal13.sr01.rk252 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.957 | 5.957
DAL13 | 1 | dal13.sr01.rk253 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.123 | 6.123
DAL13 | 1 | dal13.sr01.rk254 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.805 | 6.805
DAL13 | 1 | dal13.sr01.rk255 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.046 | 5.046
DAL13 | 1 | dal13.sr01.rk256 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.771 | 4.771
DAL13 | 1 | dal13.sr01.rk257 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.038 | 2.038
DAL13 | 1 | dal13.sr01.rk258 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.017 | 4.017
DAL13 | 1 | dal13.sr01.rk259 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.001 | 4.001
DAL13 | 1 | dal13.sr01.rk260 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.241 | 4.241
DAL13 | 1 | dal13.sr01.rk261 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk262 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.654 | 3.654
DAL13 | 1 | dal13.sr01.rk263 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.508 | 3.508
DAL13 | 1 | dal13.sr01.rk264 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.08 | 7.08
DAL13 | 1 | dal13.sr01.rk265 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.704 | 2.704
DAL13 | 1 | dal13.sr01.rk266 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.262 | 4.262
DAL13 | 1 | dal13.sr01.rk267 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk268 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk269 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk270 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk271 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk272 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk273 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk274 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk275 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk276 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk277 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk278 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk279 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk280 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk281 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk282 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk283 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk284 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk285 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk286 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk287 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk288 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk289 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk290 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk291 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk292 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk293 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk294 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk295 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk296 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk297 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk298 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk299 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk300 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk301 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk302 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk303 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk304 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk305 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk306 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk307 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk308 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk309 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk310 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk311 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk312 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk313 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk314 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk315 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk316 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk317 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk318 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk319 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk320 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk321 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk322 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk323 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk324 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk325 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk326 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk327 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk328 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk329 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk330 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Bare Metal | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk331 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk332 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk333 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk334 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk335 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk336 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk337 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk338 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk339 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk340 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk341 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | GPU | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk342 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | GPU | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk343 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk344 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk345 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk346 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk347 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk348 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk349 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Zseries | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk350 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Zseries | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk351 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Zseries | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk352 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Zseries | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk353 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Zseries | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk354 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Zseries | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk355 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk356 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk357 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk358 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk359 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk360 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk361 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk362 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk363 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk364 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk365 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk366 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk367 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk368 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk369 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk370 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk371 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk372 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk373 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk374 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk375 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk376 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk377 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk378 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk379 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk380 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk381 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk382 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk383 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk384 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk385 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk386 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk387 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen1 | Compute | Live | 10 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk388 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk399 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk400 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk401 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk402 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk403 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Management | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk404 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk405 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk406 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk407 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk408 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk409 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk410 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk411 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk412 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk413 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk414 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk415 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Bare Metal | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk416 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Bare Metal | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk417 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Bare Metal | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk418 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk419 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Build Out | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk420 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk421 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk422 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk423 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk424 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk425 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk426 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk427 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk428 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk429 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk430 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk431 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Management | Live | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk432 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk433 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk434 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 6.574 | 6.574
DAL13 | 1 | dal13.sr01.rk435 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.793 | 5.793
DAL13 | 1 | dal13.sr01.rk436 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 7.981 | 7.981
DAL13 | 1 | dal13.sr01.rk437 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 7.237 | 7.237
DAL13 | 1 | dal13.sr01.rk438 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.694 | 4.694
DAL13 | 1 | dal13.sr01.rk439 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk440 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 8.246 | 8.246
DAL13 | 1 | dal13.sr01.rk441 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 6.519 | 6.519
DAL13 | 1 | dal13.sr01.rk442 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 8.82 | 8.82
DAL13 | 1 | dal13.sr01.rk443 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 8.86 | 8.86
DAL13 | 1 | dal13.sr01.rk444 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 8.684 | 8.684
DAL13 | 1 | dal13.sr01.rk445 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 7.653 | 7.653
DAL13 | 1 | dal13.sr01.rk446 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 11.951 | 11.951
DAL13 | 1 | dal13.sr01.rk447 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 13.52 | 13.52
DAL13 | 1 | dal13.sr01.rk448 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 6.892 | 6.892
DAL13 | 1 | dal13.sr01.rk449 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.621 | 5.621
DAL13 | 1 | dal13.sr01.rk450 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk451 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 6.475 | 6.475
DAL13 | 1 | dal13.sr01.rk452 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 3.904 | 3.904
DAL13 | 1 | dal13.sr01.rk453 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.157 | 4.157
DAL13 | 1 | dal13.sr01.rk454 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 3.502 | 3.502
DAL13 | 1 | dal13.sr01.rk455 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 6.531 | 6.531
DAL13 | 1 | dal13.sr01.rk456 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 15.807 | 15.807
DAL13 | 1 | dal13.sr01.rk457 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 15.999 | 15.999
DAL13 | 1 | dal13.sr01.rk458 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 14.171 | 14.171
DAL13 | 1 | dal13.sr01.rk459 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 11.932 | 11.932
DAL13 | 1 | dal13.sr01.rk460 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 9.791 | 9.791
DAL13 | 1 | dal13.sr01.rk461 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z4-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk462 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 9.495 | 9.495
DAL13 | 1 | dal13.sr01.rk463 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.124 | 10.124
DAL13 | 1 | dal13.sr01.rk464 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 4.534 | 4.534
DAL13 | 1 | dal13.sr01.rk465 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 5.153 | 5.153
DAL13 | 1 | dal13.sr01.rk466 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.321 | 10.321
DAL13 | 1 | dal13.sr01.rk467 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.122 | 5.122
DAL13 | 1 | dal13.sr01.rk468 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.558 | 4.558
DAL13 | 1 | dal13.sr01.rk469 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.445 | 6.445
DAL13 | 1 | dal13.sr01.rk470 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.814 | 4.814
DAL13 | 1 | dal13.sr01.rk471 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.641 | 8.641
DAL13 | 1 | dal13.sr01.rk472 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk473 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.951 | 6.951
DAL13 | 1 | dal13.sr01.rk474 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.146 | 7.146
DAL13 | 1 | dal13.sr01.rk475 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.219 | 6.219
DAL13 | 1 | dal13.sr01.rk476 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.085 | 6.085
DAL13 | 1 | dal13.sr01.rk477 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.08 | 7.08
DAL13 | 1 | dal13.sr01.rk478 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.562 | 6.562
DAL13 | 1 | dal13.sr01.rk479 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.738 | 5.738
DAL13 | 1 | dal13.sr01.rk480 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.838 | 6.838
DAL13 | 1 | dal13.sr01.rk481 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.723 | 4.723
DAL13 | 1 | dal13.sr01.rk482 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.883 | 5.883
DAL13 | 1 | dal13.sr01.rk483 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk484 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.749 | 5.749
DAL13 | 1 | dal13.sr01.rk485 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.085 | 6.085
DAL13 | 1 | dal13.sr01.rk486 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.208 | 6.208
DAL13 | 1 | dal13.sr01.rk487 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.213 | 6.213
DAL13 | 1 | dal13.sr01.rk488 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.451 | 5.451
DAL13 | 1 | dal13.sr01.rk489 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 9.034 | 9.034
DAL13 | 1 | dal13.sr01.rk490 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 11.912 | 11.912
DAL13 | 1 | dal13.sr01.rk491 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 6.115 | 6.115
DAL13 | 1 | dal13.sr01.rk492 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 6.812 | 6.812
DAL13 | 1 | dal13.sr01.rk493 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.011 | 5.011
DAL13 | 1 | dal13.sr01.rk494 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk495 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 7.011 | 7.011
DAL13 | 1 | dal13.sr01.rk496 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.693 | 5.693
DAL13 | 1 | dal13.sr01.rk497 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.611 | 5.611
DAL13 | 1 | dal13.sr01.rk498 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.365 | 5.365
DAL13 | 1 | dal13.sr01.rk499 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.349 | 5.349
DAL13 | 1 | dal13.sr01.rk500 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.955 | 8.955
DAL13 | 1 | dal13.sr01.rk501 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.151 | 8.151
DAL13 | 1 | dal13.sr01.rk502 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.107 | 7.107
DAL13 | 1 | dal13.sr01.rk503 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.608 | 6.608
DAL13 | 1 | dal13.sr01.rk504 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.139 | 8.139
DAL13 | 1 | dal13.sr01.rk505 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk506 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.336 | 6.336
DAL13 | 1 | dal13.sr01.rk507 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.282 | 6.282
DAL13 | 1 | dal13.sr01.rk508 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.806 | 6.806
DAL13 | 1 | dal13.sr01.rk509 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.08 | 8.08
DAL13 | 1 | dal13.sr01.rk510 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 10.269 | 10.269
DAL13 | 1 | dal13.sr01.rk511 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 8.332 | 8.332
DAL13 | 1 | dal13.sr01.rk512 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 11.287 | 11.287
DAL13 | 1 | dal13.sr01.rk513 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 8.5 | 8.5
DAL13 | 1 | dal13.sr01.rk514 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 6.745 | 6.745
DAL13 | 1 | dal13.sr01.rk515 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 8.179 | 8.179
DAL13 | 1 | dal13.sr01.rk516 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk517 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 6.737 | 6.737
DAL13 | 1 | dal13.sr01.rk518 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.854 | 5.854
DAL13 | 1 | dal13.sr01.rk519 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.344 | 5.344
DAL13 | 1 | dal13.sr01.rk520 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 6.747 | 6.747
DAL13 | 1 | dal13.sr01.rk521 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z6-375 | 0 | 5.701 | 5.701
DAL13 | 1 | dal13.sr01.rk522 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk523 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk524 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk525 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk526 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk527 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk528 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk529 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk530 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk531 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 1 | dal13.sr01.rk532 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Live | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk533 | Dual Redundancy-3Phase | 96 | 18 | 33 | 96 | 29 | 33 | 100 | 23 | 84 | 70 | 31 | 22 | 5.2917 | 3.4828 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0.58046 | 5.74 | 5.74
DAL13 | 2 | dal13.sr02.rk534 | Redundant-3Phase | 96 | 23 | 32 | 96 | 22 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 3.2579 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0.54298 | 5.225 | 5.225
DAL13 | 2 | dal13.sr02.rk535 | Redundant-Single | 82 | 3.1 | 3.1 | 81 | 3.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 8.15 | 6.194 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 1.0323 | 6.585 | 6.585
DAL13 | 2 | dal13.sr02.rk536 | Dual Redundancy-Single | 81 | 0 | 0 | 84 | 0 | 0 | 23 | 0 | 0 | 42 | 0 | 0 | 5.75 | 8.74 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 1.4567 | 7.58 | 8.74
DAL13 | 2 | dal13.sr02.rk537 | Dual Redundancy-3Phase | 82 | 22 | 51 | 81 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 3.4224 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0.57041 | 6.574 | 6.574
DAL13 | 2 | dal13.sr02.rk538 | Redundant-3Phase | 41 | 41 | 48 | 41 | 40 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 2.8301 | Network | Aggregate | Live | 5 | Z1-375 | 0.56602 | 0 | 2.8301
DAL13 | 2 | dal13.sr02.rk539 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.867 | 4.867
DAL13 | 2 | dal13.sr02.rk540 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.974 | 5.974
DAL13 | 2 | dal13.sr02.rk541 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.959 | 5.959
DAL13 | 2 | dal13.sr02.rk542 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 7.001 | 7.001
DAL13 | 2 | dal13.sr02.rk543 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.378 | 5.378
DAL13 | 2 | dal13.sr02.rk544 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 2.906 | 2.906
DAL13 | 2 | dal13.sr02.rk545 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.277 | 5.277
DAL13 | 2 | dal13.sr02.rk546 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 7.596 | 7.596
DAL13 | 2 | dal13.sr02.rk547 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 6.207 | 6.207
DAL13 | 2 | dal13.sr02.rk548 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 3.934 | 3.934
DAL13 | 2 | dal13.sr02.rk549 | Redundant-3Phase | 41 | 41 | 40 | 40 | 40 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0167 | 2.6436 | Network | Aggregate | Live | 5 | Z1-375 | 0.52872 | 0 | 2.6436
DAL13 | 2 | dal13.sr02.rk550 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 4.843 | 4.843
DAL13 | 2 | dal13.sr02.rk551 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.348 | 5.348
DAL13 | 2 | dal13.sr02.rk552 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.521 | 5.521
DAL13 | 2 | dal13.sr02.rk553 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 2.54 | 2.54
DAL13 | 2 | dal13.sr02.rk554 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z1-375 | 0 | 5.953 | 5.953
DAL13 | 2 | dal13.sr02.rk555 | Redundant-3Phase | 35 | 61 | 64 | 33 | 37 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 2.9617 | Compute | vGPU | Live | 10 | Z1-375 | 0.29617 | 6.032 | 6.032
DAL13 | 2 | dal13.sr02.rk556 | Redundant-3Phase | 23 | 86 | 64 | 15 | 19 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 2.5888 | Compute | vGPU | Live | 10 | Z1-375 | 0.25888 | 4.926 | 4.926
DAL13 | 2 | dal13.sr02.rk557 | Redundant-3Phase | 44 | 50 | 48 | 30 | 46 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5833 | 3.0166 | Compute | vGPU | Live | 10 | Z1-375 | 0.30166 | 5.951 | 5.951
DAL13 | 2 | dal13.sr02.rk558 | Redundant-3Phase | 40 | 67 | 37 | 39 | 33 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5667 | 3.0056 | Compute | vGPU | Live | 10 | Z1-375 | 0.30056 | 5.946 | 5.946
DAL13 | 2 | dal13.sr02.rk559 | Redundant-3Phase | 32 | 44 | 59 | 31 | 67 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6667 | 3.0714 | Compute | vGPU | Live | 10 | Z1-375 | 0.30714 | 6.183 | 6.183
DAL13 | 2 | dal13.sr02.rk560 | Redundant-3Phase | 40 | 42 | 40 | 40 | 42 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0833 | 2.6875 | Network | Aggregate | Live | 5 | Z1-375 | 0.5375 | 0 | 2.6875
DAL13 | 2 | dal13.sr02.rk561 | Redundant-3Phase | 36 | 63 | 47 | 49 | 30 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6833 | 3.0824 | Compute | vGPU | Live | 10 | Z1-375 | 0.30824 | 6.248 | 6.248
DAL13 | 2 | dal13.sr02.rk562 | Redundant-3Phase | 42 | 73 | 52 | 34 | 28 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6833 | 3.0824 | Compute | vGPU | Live | 10 | Z1-375 | 0.30824 | 6.173 | 6.173
DAL13 | 2 | dal13.sr02.rk563 | Redundant-3Phase | 18 | 40 | 53 | 16 | 62 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2.6326 | Compute | vGPU | Live | 10 | Z1-375 | 0.26326 | 4.802 | 4.802
DAL13 | 2 | dal13.sr02.rk564 | Redundant-3Phase | 52 | 68 | 62 | 52 | 22 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 4.75 | 3.1263 | Compute | vGPU | Live | 10 | Z1-375 | 0.31263 | 6.061 | 6.061
DAL13 | 2 | dal13.sr02.rk565 | Redundant-3Phase | 34 | 77 | 63 | 36 | 31 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7167 | 3.1043 | Compute | vGPU | Live | 10 | Z1-375 | 0.31043 | 6.112 | 6.112
DAL13 | 2 | dal13.sr02.rk566 | Redundant-3Phase | 46 | 60 | 20 | 48 | 37 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 3.2579 | Compute | vGPU | Live | 10 | Z2-375 | 0.32579 | 6.497 | 6.497
DAL13 | 2 | dal13.sr02.rk567 | Redundant-3Phase | 48 | 67 | 62 | 60 | 30 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1667 | 3.4005 | Compute | vGPU | Live | 10 | Z2-375 | 0.34005 | 6.76 | 6.76
DAL13 | 2 | dal13.sr02.rk568 | Redundant-3Phase | 29 | 48 | 49 | 28 | 47 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 4.05 | 2.6655 | Compute | vGPU | Live | 10 | Z2-375 | 0.26655 | 5.452 | 5.452
DAL13 | 2 | dal13.sr02.rk569 | Redundant-3Phase | 34 | 57 | 51 | 33 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 4.65 | 3.0604 | Compute | vGPU | Live | 10 | Z2-375 | 0.30604 | 6.196 | 6.196
DAL13 | 2 | dal13.sr02.rk570 | Redundant-3Phase | 21 | 67 | 31 | 23 | 33 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2833 | 2.8191 | Compute | vGPU | Live | 10 | Z2-375 | 0.28191 | 5.653 | 5.653
DAL13 | 2 | dal13.sr02.rk571 | Redundant-3Phase | 41 | 43 | 41 | 40 | 41 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1333 | 2.7204 | Network | Aggregate | Live | 5 | Z2-375 | 0.54408 | 0 | 2.7204
DAL13 | 2 | dal13.sr02.rk572 | Redundant-3Phase | 31 | 60 | 40 | 29 | 36 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 3.95 | 2.5997 | Compute | vGPU | Live | 10 | Z2-375 | 0.25997 | 5.149 | 5.149
DAL13 | 2 | dal13.sr02.rk573 | Redundant-3Phase | 28 | 46 | 52 | 28 | 47 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2167 | 2.7752 | Compute | vGPU | Live | 10 | Z2-375 | 0.27752 | 5.621 | 5.621
DAL13 | 2 | dal13.sr02.rk574 | Redundant-3Phase | 38 | 51 | 61 | 38 | 61 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 3.1592 | Compute | vGPU | Live | 10 | Z2-375 | 0.31592 | 6.796 | 6.796
DAL13 | 2 | dal13.sr02.rk575 | Redundant-3Phase | 25 | 65 | 75 | 25 | 40 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5333 | 2.9837 | Compute | Hybrid | Live | 10 | Z2-375 | 0.29837 | 6.152 | 6.152
DAL13 | 2 | dal13.sr02.rk576 | Redundant-3Phase | 39 | 59 | 49 | 41 | 47 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5833 | 3.0166 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0.50276 | 6.36 | 6.36
DAL13 | 2 | dal13.sr02.rk577 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.268 | 5.268
DAL13 | 2 | dal13.sr02.rk578 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.71 | 4.71
DAL13 | 2 | dal13.sr02.rk579 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 7.107 | 7.107
DAL13 | 2 | dal13.sr02.rk580 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 6.522 | 6.522
DAL13 | 2 | dal13.sr02.rk581 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 8.662 | 8.662
DAL13 | 2 | dal13.sr02.rk582 | Redundant-3Phase | 39 | 43 | 40 | 38 | 41 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0167 | 2.6436 | Network | Aggregate | Live | 5 | Z2-375 | 0.52872 | 0 | 2.6436
DAL13 | 2 | dal13.sr02.rk583 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 6.699 | 6.699
DAL13 | 2 | dal13.sr02.rk584 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.848 | 5.848
DAL13 | 2 | dal13.sr02.rk585 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.027 | 3.027
DAL13 | 2 | dal13.sr02.rk586 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.531 | 3.531
DAL13 | 2 | dal13.sr02.rk587 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.49 | 5.49
DAL13 | 2 | dal13.sr02.rk588 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.303 | 5.303
DAL13 | 2 | dal13.sr02.rk589 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 6.764 | 6.764
DAL13 | 2 | dal13.sr02.rk590 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.907 | 5.907
DAL13 | 2 | dal13.sr02.rk591 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.582 | 4.582
DAL13 | 2 | dal13.sr02.rk592 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 3.805 | 3.805
DAL13 | 2 | dal13.sr02.rk593 | Redundant-3Phase | 39 | 41 | 39 | 39 | 42 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9833 | 2.6217 | Network | Aggregate | Live | 5 | Z2-375 | 0.52433 | 0 | 2.6217
DAL13 | 2 | dal13.sr02.rk594 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.75 | 4.75
DAL13 | 2 | dal13.sr02.rk595 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.431 | 5.431
DAL13 | 2 | dal13.sr02.rk596 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.621 | 5.621
DAL13 | 2 | dal13.sr02.rk597 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 4.702 | 4.702
DAL13 | 2 | dal13.sr02.rk598 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z2-375 | 0 | 5.563 | 5.563
DAL13 | 2 | dal13.sr02.rk599 | Redundant-3Phase | 84 | 116 | 117 | 84 | 115 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5333 | 6.9326 | Compute | Hybrid | Live | 10 | Z3-375 | 0.69326 | 14.666 | 14.666
DAL13 | 2 | dal13.sr02.rk600 | Redundant-3Phase | 72 | 81 | 84 | 73 | 83 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 7.85 | 5.1666 | Compute | Hybrid | Live | 10 | Z3-375 | 0.51666 | 10.452 | 10.452
DAL13 | 2 | dal13.sr02.rk601 | Redundant-3Phase | 110 | 105 | 89 | 109 | 103 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9833 | 6.5706 | Compute | Hybrid | Live | 10 | Z3-375 | 0.65706 | 13.782 | 13.782
DAL13 | 2 | dal13.sr02.rk602 | Redundant-3Phase | 68 | 85 | 81 | 68 | 83 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7667 | 5.1117 | Compute | Hybrid | Live | 10 | Z3-375 | 0.51117 | 10.229 | 10.229
DAL13 | 2 | dal13.sr02.rk603 | Redundant-3Phase | 70 | 89 | 79 | 69 | 88 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 5.1995 | Compute | Hybrid | Live | 10 | Z3-375 | 0.51995 | 11.097 | 11.097
DAL13 | 2 | dal13.sr02.rk604 | Redundant-3Phase | 50 | 42 | 47 | 50 | 44 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6833 | 3.0824 | Network | Aggregate | Live | 5 | Z3-375 | 0.61648 | 0 | 3.0824
DAL13 | 2 | dal13.sr02.rk605 | Redundant-3Phase | 82 | 95 | 86 | 80 | 94 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7333 | 5.7479 | Compute | Hybrid | Live | 10 | Z3-375 | 0.57479 | 12.338 | 12.338
DAL13 | 2 | dal13.sr02.rk606 | Redundant-3Phase | 72 | 106 | 67 | 72 | 102 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 8.25 | 5.4298 | Compute | Hybrid | Live | 10 | Z3-375 | 0.54298 | 11.554 | 11.554
DAL13 | 2 | dal13.sr02.rk607 | Redundant-3Phase | 81 | 96 | 70 | 80 | 96 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2333 | 5.4189 | Compute | Hybrid | Live | 10 | Z3-375 | 0.54189 | 11.679 | 11.679
DAL13 | 2 | dal13.sr02.rk608 | Redundant-3Phase | 96 | 106 | 101 | 80 | 100 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4833 | 6.2416 | Compute | Hybrid | Live | 10 | Z3-375 | 0.62416 | 13.453 | 13.453
DAL13 | 2 | dal13.sr02.rk609 | Redundant-3Phase | 16 | 59 | 29 | 15 | 52 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 2.3036 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.38393 | 4.47 | 4.47
DAL13 | 2 | dal13.sr02.rk610 | Redundant-3Phase | 47 | 50 | 38 | 46 | 48 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4333 | 2.9178 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.48631 | 6.254 | 6.254
DAL13 | 2 | dal13.sr02.rk611 | Redundant-3Phase | 31 | 44 | 62 | 35 | 43 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4833 | 2.9508 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.49179 | 6.284 | 6.284
DAL13 | 2 | dal13.sr02.rk612 | Redundant-3Phase | 74 | 69 | 58 | 80 | 65 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7333 | 4.4316 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.7386 | 9.182 | 9.182
DAL13 | 2 | dal13.sr02.rk613 | Redundant-3Phase | 66 | 26 | 60 | 59 | 23 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8833 | 3.214 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.53567 | 6.73 | 6.73
DAL13 | 2 | dal13.sr02.rk614 | Redundant-3Phase | 47 | 47 | 47 | 47 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 3.0934 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.51556 | 6.428 | 6.428
DAL13 | 2 | dal13.sr02.rk615 | Redundant-3Phase | 44 | 42 | 42 | 43 | 43 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 4.25 | 2.7972 | Network | Aggregate | Live | 5 | Z3-375 | 0.55944 | 0 | 2.7972
DAL13 | 2 | dal13.sr02.rk616 | Redundant-3Phase | 0 | 0 | 0 | 61 | 58 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7333 | 3.7735 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.62891 | 3.993 | 3.993
DAL13 | 2 | dal13.sr02.rk617 | Redundant-3Phase | 53 | 47 | 47 | 52 | 49 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9167 | 3.236 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.53933 | 6.852 | 6.852
DAL13 | 2 | dal13.sr02.rk618 | Redundant-3Phase | 82 | 50 | 55 | 70 | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1167 | 4.0257 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.67096 | 8.18 | 8.18
DAL13 | 2 | dal13.sr02.rk619 | Redundant-3Phase | 40 | 42 | 31 | 38 | 41 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7167 | 2.4462 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.40769 | 5.208 | 5.208
DAL13 | 2 | dal13.sr02.rk620 | Redundant-3Phase | 56 | 41 | 50 | 55 | 41 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8833 | 3.214 | Bare Metal | Bare Metal | Live | 6 | Z3-375 | 0.53567 | 7.029 | 7.029
DAL13 | 2 | dal13.sr02.rk621 | Redundant-3Phase | 54 | 43 | 43 | 54 | 43 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6667 | 3.0714 | Gen2 | GPU | Live | 20 | Z1-375 | 0.15357 | 0 | 3.0714
DAL13 | 2 | dal13.sr02.rk622 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk623 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk624 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk625 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | GPU | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk626 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | GPU | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk630 | Redundant-3Phase | 86 | 70 | 85 | 86 | 72 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0333 | 5.2872 | Gen2 | Compute | Live | 20 | Z2-375 | 0.26436 | 0 | 5.2872
DAL13 | 2 | dal13.sr02.rk631 | Redundant-3Phase | 86 | 73 | 84 | 87 | 73 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1167 | 5.3421 | Gen2 | Compute | Live | 20 | Z2-375 | 0.2671 | 0 | 5.3421
DAL13 | 2 | dal13.sr02.rk632 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk633 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk634 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk635 | Redundant-3Phase | 48 | 0 | 17 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.125 | 1.3986 | Storage | File/Block | Live | 6 | Z3-375 | 0.2331 | 0 | 1.3986
DAL13 | 2 | dal13.sr02.rk636 | Redundant-3Phase | 46 | 26 | 16 | 50 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1.9745 | Storage | File/Block | Live | 6 | Z3-375 | 0.32908 | 0 | 1.9745
DAL13 | 2 | dal13.sr02.rk637 | Redundant-3Phase | 47 | 0 | 10 | 47 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 1.8758 | Storage | File/Block | Live | 6 | Z3-375 | 0.31263 | 0 | 1.8758
DAL13 | 2 | dal13.sr02.rk638 | Redundant-3Phase | 10 | 0 | 54 | 10 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 2.0732 | Storage | File/Block | Live | 6 | Z3-375 | 0.34553 | 0 | 2.0732
DAL13 | 2 | dal13.sr02.rk639 | Redundant-3Phase | 25 | 25 | 48 | 25 | 25 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2167 | 2.1171 | Storage | File/Block | Live | 6 | Z3-375 | 0.35285 | 0 | 2.1171
DAL13 | 2 | dal13.sr02.rk640 | Redundant-3Phase | 23 | 28 | 18 | 22 | 25 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2333 | 1.4699 | Storage | File/Block | Live | 6 | Z3-375 | 0.24498 | 0 | 1.4699
DAL13 | 2 | dal13.sr02.rk641 | Redundant-3Phase | 23 | 27 | 45 | 23 | 27 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1333 | 2.0622 | Storage | File/Block | Live | 6 | Z3-375 | 0.34371 | 0 | 2.0622
DAL13 | 2 | dal13.sr02.rk642 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk643 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 6 | Z3-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk644 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Fiber | Live | 0 | Unknown | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk645 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Planned | 0 | Unknown | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk646 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Planned | 0 | Unknown | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk647 | Redundant-3Phase | 20 | 20 | 40 | 20 | 20 | 40 | 20 | 40 | 20 | 20 | 40 | 20 | 2.6667 | 1.7551 | Network | Router | Live | 9.1 | Unknown | 0.19287 | 0 | 1.7551
DAL13 | 2 | dal13.sr02.rk648 | Redundant-3Phase | 20 | 20 | 40 | 20 | 20 | 40 | 20 | 40 | 20 | 20 | 40 | 20 | 2.6667 | 1.7551 | Network | Router | Live | 9.1 | Unknown | 0.19287 | 0 | 1.7551
DAL13 | 2 | dal13.sr02.rk649 | Redundant-3Phase | 32 | 31 | 54 | 32 | 32 | 54 | 32 | 64 | 32 | 32 | 64 | 32 | 3.9167 | 2.5778 | Network | Router | Live | 9.1 | Unknown | 0.28327 | 0 | 2.5778
DAL13 | 2 | dal13.sr02.rk650 | Redundant-3Phase | 28 | 28 | 56 | 28 | 28 | 56 | 28 | 56 | 28 | 28 | 56 | 28 | 3.7333 | 2.4571 | Network | Router | Live | 9.1 | Unknown | 0.27001 | 0 | 2.4571
DAL13 | 2 | dal13.sr02.rk651 | Redundant-3Phase | 17 | 28 | 13 | 17 | 28 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9333 | 1.2724 | Fabric | Server | Live | 4.6 | Unknown | 0.27662 | 0 | 1.2724
DAL13 | 2 | dal13.sr02.rk652 | Redundant-3Phase | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1 | 0.65816 | Network | Firewall | Live | 6 | Unknown | 0.10969 | 0 | 0.65816
DAL13 | 2 | dal13.sr02.rk653 | Redundant-3Phase | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65816 | Fabric | Server | Live | 4.6 | Unknown | 0.14308 | 0 | 0.65816
DAL13 | 2 | dal13.sr02.rk654 | Redundant-3Phase | 0 | 33 | 33 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 3.3 | 2.1719 | Network | Router | Live | 9.1 | Unknown | 0.23867 | 0 | 2.1719
DAL13 | 2 | dal13.sr02.rk655 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Planned | 0 | Unknown | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk656 | Redundant-3Phase | 44 | 47 | 54 | 44 | 43 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8167 | 3.1701 | Gen2 | GPU | Live | 20 | Z4-375 | 0.15851 | 0 | 3.1701
DAL13 | 2 | dal13.sr02.rk657 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk658 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk659 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk660 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | GPU | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk661 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | GPU | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk662 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk663 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk664 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk665 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk666 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk667 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.844 | 10.844
DAL13 | 2 | dal13.sr02.rk668 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.369 | 10.369
DAL13 | 2 | dal13.sr02.rk669 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 9.893 | 9.893
DAL13 | 2 | dal13.sr02.rk670 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.623 | 10.623
DAL13 | 2 | dal13.sr02.rk671 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 5.563 | 5.563
DAL13 | 2 | dal13.sr02.rk672 | Redundant-3Phase | 53 | 46 | 48 | 51 | 47 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 3.225 | Network | Aggregate | Live | 5 | Z4-375 | 0.645 | 0 | 3.225
DAL13 | 2 | dal13.sr02.rk673 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.687 | 10.687
DAL13 | 2 | dal13.sr02.rk674 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.192 | 10.192
DAL13 | 2 | dal13.sr02.rk675 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 10.879 | 10.879
DAL13 | 2 | dal13.sr02.rk676 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 6.239 | 6.239
DAL13 | 2 | dal13.sr02.rk677 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 10 | Z4-375 | 0 | 12.66 | 12.66
DAL13 | 2 | dal13.sr02.rk678 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.855 | 5.855
DAL13 | 2 | dal13.sr02.rk679 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.441 | 4.441
DAL13 | 2 | dal13.sr02.rk680 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.727 | 4.727
DAL13 | 2 | dal13.sr02.rk681 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.221 | 4.221
DAL13 | 2 | dal13.sr02.rk682 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.37 | 5.37
DAL13 | 2 | dal13.sr02.rk683 | Redundant-3Phase | 40 | 62 | 20 | 40 | 62 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0667 | 2.6765 | Network | Aggregate | Live | 5 | Z4-375 | 0.5353 | 0 | 2.6765
DAL13 | 2 | dal13.sr02.rk684 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.734 | 5.734
DAL13 | 2 | dal13.sr02.rk685 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.604 | 4.604
DAL13 | 2 | dal13.sr02.rk686 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 5.27 | 5.27
DAL13 | 2 | dal13.sr02.rk687 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 4.905 | 4.905
DAL13 | 2 | dal13.sr02.rk688 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z4-375 | 0 | 6.521 | 6.521
DAL13 | 2 | dal13.sr02.rk689 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.275 | 8.275
DAL13 | 2 | dal13.sr02.rk690 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.326 | 5.326
DAL13 | 2 | dal13.sr02.rk691 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.471 | 6.471
DAL13 | 2 | dal13.sr02.rk692 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.837 | 6.837
DAL13 | 2 | dal13.sr02.rk693 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.559 | 5.559
DAL13 | 2 | dal13.sr02.rk694 | Redundant-3Phase | 40 | 42 | 42 | 41 | 42 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1833 | 2.7533 | Network | Aggregate | Live | 5 | Z5-375 | 0.55066 | 0 | 2.7533
DAL13 | 2 | dal13.sr02.rk695 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.607 | 7.607
DAL13 | 2 | dal13.sr02.rk696 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.684 | 5.684
DAL13 | 2 | dal13.sr02.rk697 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.111 | 7.111
DAL13 | 2 | dal13.sr02.rk698 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.925 | 5.925
DAL13 | 2 | dal13.sr02.rk699 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.13 | 8.13
DAL13 | 2 | dal13.sr02.rk700 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 13.914 | 13.914
DAL13 | 2 | dal13.sr02.rk701 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 14.712 | 14.712
DAL13 | 2 | dal13.sr02.rk702 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 11.938 | 11.938
DAL13 | 2 | dal13.sr02.rk703 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.774 | 7.774
DAL13 | 2 | dal13.sr02.rk704 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 10.003 | 10.003
DAL13 | 2 | dal13.sr02.rk705 | Redundant-3Phase | 47 | 39 | 43 | 47 | 38 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2667 | 2.8081 | Network | Aggregate | Live | 5 | Z5-375 | 0.56163 | 0 | 2.8081
DAL13 | 2 | dal13.sr02.rk706 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.873 | 6.873
DAL13 | 2 | dal13.sr02.rk707 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 8.575 | 8.575
DAL13 | 2 | dal13.sr02.rk708 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.721 | 5.721
DAL13 | 2 | dal13.sr02.rk709 | Redundant-3Phase | 21 | 37 | 33 | 15 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8333 | 1.8648 | Network | Ded. Firewall | Live | 6 | Z5-375 | 0.3108 | 2.106 | 2.106
DAL13 | 2 | dal13.sr02.rk710 | Redundant-3Phase | 10 | 21 | 12 | 10 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3333 | 0.87755 | Bare Metal | COD | Live | 6 | Z5-375 | 0.14626 | 1.214 | 1.214
DAL13 | 2 | dal13.sr02.rk711 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk712 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Bare Metal | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk713 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk714 | Redundant-3Phase | 0 | 23 | 20 | 0 | 21 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 1.4809 | NGDC | Network | Planned | 15 | Z6-375 | 0.098724 | 0 | 1.4809
DAL13 | 2 | dal13.sr02.rk715 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk716 | Redundant-3Phase | 0 | 31 | 30 | 0 | 29 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 3.025 | 1.9909 | NGDC | Network | Planned | 15 | Z6-375 | 0.13273 | 0 | 1.9909
DAL13 | 2 | dal13.sr02.rk717 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Live | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk718 | Redundant-3Phase | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1 | 0.65816 | NGDC | Network | Planned | 15 | Z6-375 | 0.043877 | 0 | 0.65816
DAL13 | 2 | dal13.sr02.rk719 | Redundant-3Phase | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 1 | 0.65816 | NGDC | Network | Planned | 15 | Z6-375 | 0.043877 | 0 | 0.65816
DAL13 | 2 | dal13.sr02.rk720 | Redundant-3Phase | 20 | 18 | 19 | 19 | 21 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1.95 | 1.2834 | NGDC | Network | Planned | 15 | Z6-375 | 0.085561 | 0 | 1.2834
DAL13 | 2 | dal13.sr02.rk721 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Fiber | Planned | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk722 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.817 | 4.817
DAL13 | 2 | dal13.sr02.rk723 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 6.622 | 6.622
DAL13 | 2 | dal13.sr02.rk724 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.299 | 4.299
DAL13 | 2 | dal13.sr02.rk725 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.941 | 4.941
DAL13 | 2 | dal13.sr02.rk726 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.366 | 3.366
DAL13 | 2 | dal13.sr02.rk727 | Redundant-3Phase | 44 | 40 | 38 | 43 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0167 | 2.6436 | Network | Aggregate | Live | 5 | Z5-375 | 0.52872 | 0 | 2.6436
DAL13 | 2 | dal13.sr02.rk728 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 5.283 | 5.283
DAL13 | 2 | dal13.sr02.rk729 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.585 | 2.585
DAL13 | 2 | dal13.sr02.rk730 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 9.076 | 9.076
DAL13 | 2 | dal13.sr02.rk731 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 10.282 | 10.282
DAL13 | 2 | dal13.sr02.rk732 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 12.841 | 12.841
DAL13 | 2 | dal13.sr02.rk733 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk734 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk735 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk736 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk737 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk738 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk739 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | File/Block | Planned | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk740 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | File/Block | Planned | 6 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk741 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk742 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk743 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk744 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk745 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk746 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk747 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk748 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk749 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk750 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk751 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk752 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk753 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 2 | dal13.sr02.rk754 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z6-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk01 | Dual Redundancy-3Phase | 96 | 18 | 33 | 96 | 29 | 33 | 100 | 23 | 84 | 70 | 31 | 22 | 5.2917 | 3.4828 | Bare Metal | VDC | Power Limit | 5 | Z6-375 | 0.69655 | 6.738 | 6.738
DAL13 | 3 | dal13.sr03.rk02 | Redundant-3Phase | 96 | 23 | 32 | 96 | 22 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 3.2579 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0.65158 | 4.388 | 4.388
DAL13 | 3 | dal13.sr03.rk03 | Redundant-Single | 82 | 3.1 | 3.1 | 81 | 3.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 8.15 | 6.194 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 1.2388 | 3.478 | 6.194
DAL13 | 3 | dal13.sr03.rk04 | Dual Redundancy-Single | 81 | 0 | 0 | 84 | 0 | 0 | 23 | 0 | 0 | 42 | 0 | 0 | 5.75 | 8.74 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 1.748 | 2.401 | 8.74
DAL13 | 3 | dal13.sr03.rk05 | Dual Redundancy-3Phase | 82 | 22 | 51 | 81 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 3.4224 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0.68449 | 2.709 | 3.4224
DAL13 | 3 | dal13.sr03.rk06 | Single-Single | 222 | 252 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2 | 8.436 | Network | Aggregate | Power Limit | 5 | Z6-375 | 1.6872 | 0 | 8.436
DAL13 | 3 | dal13.sr03.rk07 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 2.596 | 2.596
DAL13 | 3 | dal13.sr03.rk08 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.137 | 3.137
DAL13 | 3 | dal13.sr03.rk09 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.895 | 5.895
DAL13 | 3 | dal13.sr03.rk10 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 10.313 | 10.313
DAL13 | 3 | dal13.sr03.rk11 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 8.718 | 8.718
DAL13 | 3 | dal13.sr03.rk12 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.566 | 3.566
DAL13 | 3 | dal13.sr03.rk13 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 4.894 | 4.894
DAL13 | 3 | dal13.sr03.rk14 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.161 | 5.161
DAL13 | 3 | dal13.sr03.rk15 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 4.857 | 4.857
DAL13 | 3 | dal13.sr03.rk16 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.053 | 5.053
DAL13 | 3 | dal13.sr03.rk17 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Power Limit | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk18 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.334 | 3.334
DAL13 | 3 | dal13.sr03.rk19 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.391 | 5.391
DAL13 | 3 | dal13.sr03.rk20 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 4.073 | 4.073
DAL13 | 3 | dal13.sr03.rk21 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.017 | 5.017
DAL13 | 3 | dal13.sr03.rk22 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 4.667 | 4.667
DAL13 | 3 | dal13.sr03.rk23 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.126 | 3.126
DAL13 | 3 | dal13.sr03.rk24 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.163 | 3.163
DAL13 | 3 | dal13.sr03.rk25 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 2.81 | 2.81
DAL13 | 3 | dal13.sr03.rk26 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.693 | 5.693
DAL13 | 3 | dal13.sr03.rk27 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.153 | 3.153
DAL13 | 3 | dal13.sr03.rk28 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Power Limit | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk29 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 2.796 | 2.796
DAL13 | 3 | dal13.sr03.rk30 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.332 | 3.332
DAL13 | 3 | dal13.sr03.rk31 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.669 | 3.669
DAL13 | 3 | dal13.sr03.rk32 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.835 | 5.835
DAL13 | 3 | dal13.sr03.rk33 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 1.033 | 1.033
DAL13 | 3 | dal13.sr03.rk34 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 6.644 | 6.644
DAL13 | 3 | dal13.sr03.rk35 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 2.681 | 2.681
DAL13 | 3 | dal13.sr03.rk36 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 2.979 | 2.979
DAL13 | 3 | dal13.sr03.rk37 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 2.989 | 2.989
DAL13 | 3 | dal13.sr03.rk38 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 1.465 | 1.465
DAL13 | 3 | dal13.sr03.rk39 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Power Limit | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk40 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 5.446 | 5.446
DAL13 | 3 | dal13.sr03.rk41 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 7.822 | 7.822
DAL13 | 3 | dal13.sr03.rk42 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 4.967 | 4.967
DAL13 | 3 | dal13.sr03.rk43 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 3.107 | 3.107
DAL13 | 3 | dal13.sr03.rk44 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 5 | Z6-375 | 0 | 4.913 | 4.913
DAL13 | 3 | dal13.sr03.rk45 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 3.707 | 3.707
DAL13 | 3 | dal13.sr03.rk46 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 4.254 | 4.254
DAL13 | 3 | dal13.sr03.rk47 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 4.867 | 4.867
DAL13 | 3 | dal13.sr03.rk48 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 2.615 | 2.615
DAL13 | 3 | dal13.sr03.rk49 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 5.72 | 5.72
DAL13 | 3 | dal13.sr03.rk50 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk51 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 3.422 | 3.422
DAL13 | 3 | dal13.sr03.rk52 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 2.311 | 2.311
DAL13 | 3 | dal13.sr03.rk53 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 4.72 | 4.72
DAL13 | 3 | dal13.sr03.rk54 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 4.865 | 4.865
DAL13 | 3 | dal13.sr03.rk55 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 9 | Z6-375 | 0 | 0.279 | 0.279
DAL13 | 3 | dal13.sr03.rk56 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 12.915 | 12.915
DAL13 | 3 | dal13.sr03.rk57 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 5.382 | 5.382
DAL13 | 3 | dal13.sr03.rk58 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 4.195 | 4.195
DAL13 | 3 | dal13.sr03.rk59 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 10.345 | 10.345
DAL13 | 3 | dal13.sr03.rk60 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 13.043 | 13.043
DAL13 | 3 | dal13.sr03.rk61 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Power Limit | 5 | Z6-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk62 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 13.509 | 13.509
DAL13 | 3 | dal13.sr03.rk63 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 12.545 | 12.545
DAL13 | 3 | dal13.sr03.rk64 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 11.51 | 11.51
DAL13 | 3 | dal13.sr03.rk65 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 8.979 | 8.979
DAL13 | 3 | dal13.sr03.rk66 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Power Limit | 9 | Z6-375 | 0 | 7.703 | 7.703
DAL13 | 3 | dal13.sr03.rk67 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 3.605 | 3.605
DAL13 | 3 | dal13.sr03.rk68 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 4.746 | 4.746
DAL13 | 3 | dal13.sr03.rk69 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 5.132 | 5.132
DAL13 | 3 | dal13.sr03.rk70 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 4.501 | 4.501
DAL13 | 3 | dal13.sr03.rk71 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 4.852 | 4.852
DAL13 | 3 | dal13.sr03.rk72 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk73 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 6.693 | 6.693
DAL13 | 3 | dal13.sr03.rk74 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 4.061 | 4.061
DAL13 | 3 | dal13.sr03.rk75 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 3.383 | 3.383
DAL13 | 3 | dal13.sr03.rk76 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 5.283 | 5.283
DAL13 | 3 | dal13.sr03.rk77 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Compute | Hybrid | Live | 5 | Z5-375 | 0 | 4.478 | 4.478
DAL13 | 3 | dal13.sr03.rk78 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 4.512 | 4.512
DAL13 | 3 | dal13.sr03.rk79 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 6.335 | 6.335
DAL13 | 3 | dal13.sr03.rk80 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 5.255 | 5.255
DAL13 | 3 | dal13.sr03.rk81 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 6.853 | 6.853
DAL13 | 3 | dal13.sr03.rk82 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 6.562 | 6.562
DAL13 | 3 | dal13.sr03.rk83 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk84 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 5.179 | 5.179
DAL13 | 3 | dal13.sr03.rk85 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 8.158 | 8.158
DAL13 | 3 | dal13.sr03.rk86 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 2.19 | 2.19
DAL13 | 3 | dal13.sr03.rk87 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 5.039 | 5.039
DAL13 | 3 | dal13.sr03.rk88 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 7.7 | Z5-375 | 0 | 3.858 | 3.858
DAL13 | 3 | dal13.sr03.rk89 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Ded. Firewall | Live | 6 | Z5-375 | 0 | 1.491 | 1.491
DAL13 | 3 | dal13.sr03.rk90 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.437 | 4.437
DAL13 | 3 | dal13.sr03.rk91 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 7.275 | 7.275
DAL13 | 3 | dal13.sr03.rk92 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.366 | 4.366
DAL13 | 3 | dal13.sr03.rk93 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.703 | 3.703
DAL13 | 3 | dal13.sr03.rk94 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk95 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.23 | 4.23
DAL13 | 3 | dal13.sr03.rk96 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 1.676 | 1.676
DAL13 | 3 | dal13.sr03.rk97 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.102 | 4.102
DAL13 | 3 | dal13.sr03.rk98 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.597 | 3.597
DAL13 | 3 | dal13.sr03.rk99 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.318 | 4.318
DAL13 | 3 | dal13.sr03.rk100 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.117 | 3.117
DAL13 | 3 | dal13.sr03.rk101 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.147 | 3.147
DAL13 | 3 | dal13.sr03.rk102 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.293 | 3.293
DAL13 | 3 | dal13.sr03.rk103 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.727 | 3.727
DAL13 | 3 | dal13.sr03.rk104 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 3.717 | 3.717
DAL13 | 3 | dal13.sr03.rk105 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk106 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.969 | 2.969
DAL13 | 3 | dal13.sr03.rk107 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 1.303 | 1.303
DAL13 | 3 | dal13.sr03.rk108 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 4.297 | 4.297
DAL13 | 3 | dal13.sr03.rk109 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.35 | 2.35
DAL13 | 3 | dal13.sr03.rk110 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 6 | Z5-375 | 0 | 2.264 | 2.264
DAL13 | 3 | dal13.sr03.rk111 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.696 | 2.696
DAL13 | 3 | dal13.sr03.rk112 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 4.559 | 4.559
DAL13 | 3 | dal13.sr03.rk113 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.029 | 2.029
DAL13 | 3 | dal13.sr03.rk114 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 3.24 | 3.24
DAL13 | 3 | dal13.sr03.rk115 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.926 | 2.926
DAL13 | 3 | dal13.sr03.rk116 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk117 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 6.923 | 6.923
DAL13 | 3 | dal13.sr03.rk118 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.374 | 2.374
DAL13 | 3 | dal13.sr03.rk119 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.575 | 2.575
DAL13 | 3 | dal13.sr03.rk120 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 1.296 | 1.296
DAL13 | 3 | dal13.sr03.rk121 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 1.974 | 1.974
DAL13 | 3 | dal13.sr03.rk122 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 0.884 | 0.884
DAL13 | 3 | dal13.sr03.rk123 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 1.694 | 1.694
DAL13 | 3 | dal13.sr03.rk124 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.35 | 2.35
DAL13 | 3 | dal13.sr03.rk125 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.242 | 2.242
DAL13 | 3 | dal13.sr03.rk126 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.281 | 2.281
DAL13 | 3 | dal13.sr03.rk127 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Aggregate | Live | 5 | Z5-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk128 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.924 | 2.924
DAL13 | 3 | dal13.sr03.rk129 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.913 | 2.913
DAL13 | 3 | dal13.sr03.rk130 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 3.34 | 3.34
DAL13 | 3 | dal13.sr03.rk131 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.143 | 2.143
DAL13 | 3 | dal13.sr03.rk132 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Bare Metal | Bare Metal | Live | 5 | Z5-375 | 0 | 2.891 | 2.891
DAL13 | 3 | dal13.sr03.rk133 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk134 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk135 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk136 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk137 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unknown | Unknown | Unknown | 0 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk138 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk139 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk140 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk141 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk142 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk143 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk144 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk145 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk146 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk147 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk148 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk149 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk150 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk151 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk152 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk153 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk154 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk155 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk156 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk157 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk158 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk159 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk160 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk161 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk162 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk163 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk164 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk165 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk166 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk167 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk168 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk169 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk170 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk171 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk172 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk173 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk174 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk175 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk176 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk177 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk178 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk179 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk180 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk181 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk182 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk183 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk184 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk185 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk186 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk187 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PowerVS | PowerVS | Planned | 11.8 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk188 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk189 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk190 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk191 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk192 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk193 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk194 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk195 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk196 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk197 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk198 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Router | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk199 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Lab | Live | 9.5 | Z4-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk200 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk201 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk202 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk203 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk204 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk205 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk206 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk207 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk208 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk209 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk210 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk211 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk212 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk213 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk214 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk215 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk216 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk217 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk218 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk219 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk220 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk221 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk222 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 2.9 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk223 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk224 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk225 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk226 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk227 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk228 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk229 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk230 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Live | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk231 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk232 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk233 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | File/Block | Planned | 3.2 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk234 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Planned | 14 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk235 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Planned | 14 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk236 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Planned | 14 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk237 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Storage | COS | Planned | 14 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk238 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk239 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk240 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk241 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk242 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk243 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk244 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk245 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Live | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk246 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Live | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk247 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Live | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk248 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Live | 15 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk249 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk250 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk251 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk252 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk253 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk254 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk255 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk256 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk257 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk258 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk259 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk260 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk261 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk262 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk263 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk264 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk265 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk266 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z3-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk267 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk268 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Bare Metal | Planned | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk269 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk270 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk271 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk272 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk273 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk274 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk275 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk276 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk277 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk278 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk279 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk280 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Acadia | Planned | 15 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk281 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk282 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk283 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk284 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk285 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk286 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk287 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk288 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk289 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk290 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk291 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk292 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk293 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk294 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk295 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk296 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk297 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk298 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk299 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk300 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk301 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk302 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk303 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk304 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk305 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk306 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk307 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk308 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk309 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk310 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk311 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk312 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk313 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk314 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk315 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk316 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk317 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk318 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk319 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk320 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk321 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk322 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk323 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk324 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Unknown | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk325 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk326 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk327 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk328 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk329 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk330 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk331 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk332 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z2-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk333 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Network | Fiber | Planned | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk334 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk335 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk336 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk337 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk338 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk339 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk340 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk341 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Network | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk342 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk343 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk344 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk345 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Network | Live | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk346 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk347 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk348 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk349 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk350 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk351 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk352 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk353 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk354 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk355 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk356 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk357 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk358 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Management | Planned | 15 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk359 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | File/Block | Planned | 6 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk360 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | File/Block | Planned | 6 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk361 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk362 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk363 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk364 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk365 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk366 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk367 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk368 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk369 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NGDC | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk370 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk371 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk372 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk373 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk374 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk375 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk376 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk377 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk378 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk379 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk380 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk381 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk382 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk383 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk384 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk385 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk386 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk387 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk388 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Live | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk389 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk390 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gen2 | Compute | Planned | 20 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk391 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk392 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk393 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk394 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk395 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk396 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk397 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0
DAL13 | 3 | dal13.sr03.rk398 | Redundant-3Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unallocated | Unallocated | Power Limit | 0 | Z1-375 | 0 | 0 | 0

## power_data.old (hidden)
Rack | Lookup | PDU | Busway | Circuit | CircuitMR | 1 | 2 | 3 | Strip | L1 Phase Amps (MAX 12A) | L2 Phase Amps (MAX 12A) | L3 Phase Amps (MAX 12A) | L1-L3 Phase Max Amps | Total 3 Phase Amp | Total kW (Max 15.4) | Zone | Planned kW | Type | Power Strips? | SR
1 | 1G | T201.1 | UDP201.1A | [5 empty] | G | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | Row 1 - Compute (NG2) | No | 0
NEEDS TO BE AUTOMATED WITH MASTER RACK POWER CALCULATOR FILE.

## ppr
Rack Attributes |  |  | Power per Rack (kW)
Group | Type | Sub-Type | kW (Single) | KW (3-Phase) | Note
Sellable | Bare Metal | Bare Metal | 5 | 6 | 25G will use 9kW per rack.
Sellable | Bare Metal | COD | 5 | 6
Sellable | Bare Metal | Microcloud | 5 | 6
Sellable | Bare Metal | Power8 | 5 | 6
Sellable | Bare Metal | VDC | 5 | 6
Sellable | Compute | Hybrid | 5 | 10
Sellable | Compute | Local | 5 | 10
Sellable | PowerVS | PowerVS | 0 | 11.8 | Value generalized for attribute update. True usage is 13kW for 10 rack deployment. If 12 rack deployment with Power10 servers, the two additional racks use 15kW. IE. 130 + 30 = 160kW per row
Sellable | Compute | SAN | 5 | 10
Sellable | Compute | vGPU | 5 | 10
Sellable | Gen1 | Compute | 0 | 10
Sellable | Gen2 | Bare Metal | 0 | 20
Sellable | Gen2 | Compute | 0 | 20
Sellable | Gen2 | GPU | 0 | 20
Sellable | Gen2 | Acadia | 0 | 15 | 60kW per 4 rack deployment (Formerly Storage)
Sellable | Gen2 | COS | 0 | 14 | Typically only a 4 rack deployment
Sellable | Gen2 | File/Block | 0 | 6
Sellable | Gen2 | Zseries | 0 | 10
Sellable | Network | Ded. Firewall | 5 | 6
Sellable | Network | Firewall | 5 | 6
Sellable | Network | Load Balancer | 5 | 6
Sellable | Storage | COS | 5 | 6
Sellable | Storage | File/Block | 5 | 6
Sellable | Storage | Misc. | 5 | 6
Sellable | Storage | Swift | 5 | 6
Sellable | Unallocated | Unallocated | 0 | 0
Unsellable | Fabric | DTS | 4.6 | 4.6
Unsellable | Fabric | Lab | 4.6 | 4.6
Unsellable | Fabric | Misc. | 4.6 | 4.6
Unsellable | Fabric | Server | 4.6 | 4.6
Unsellable | Fabric | Unallocated | 4.6 | 4.6
Unsellable | Gen1 | Management | 0 | 15
Unsellable | Gen1 | Network | 0 | 15
Unsellable | Gen2 | Management | 0 | 15
Unsellable | Gen2 | Network | 0 | 15
Unsellable | Network | Aggregate | 5 | 5
Unsellable | Network | Fiber | 0 | 0
Unsellable | Network | Lab | 9.1 | 9.1
Unsellable | Network | Misc. | 9.1 | 9.1
Unsellable | Network | Network Spares | 0 | 0
Unsellable | Network | Router | 9.1 | 9.1
Unsellable | Network | Unallocated | 9.1 | 9.1
Sellable | NGDC | Compute | 0 | 20
Sellable | NGDC | Bare Metal | 0 | 20
Sellable | NGDC | Acadia | 0 | 15 | Formerly Storage
Sellable | NGDC | Z Mainframe | 0 | 10
Sellable | NGDC | COS | 0 | 14
Sellable | NGDC | File/Block | 0 | 6
Unsellable | NGDC | Management | 0 | 15
Unsellable | NGDC | Network | 0 | 15

## file_path (hidden)
File | File Path | power_date | Data Center | Server Room | Vendor Identification | Max Power | Details
Datacenter | DAL13 | 2024-02-27 | DAL13 | 1 | Data Hall 4 | 4500 | 400/30/3Phase
Current File Path | C:\Users\4G5597897\Box\IBM Cloud Capacity\DC Files\Rack and Power Allocation Assessment\ |  | DAL13 | 1 | Data Hall 4 | 4500 | 400/30/3Phase
Capacity Summary Report | C:\Users\4G5597897\Box\IBM Cloud Capacity\ | Data Date | DAL13 | 2 | Data Hall 3 | 2250 | 400/30/3Phase
Rack Breakdown - MASTER | C:\Users\4G5597897\Box\IBM Cloud Capacity\Capacity Management - Shared Reports\DC Manager Files\ | Data as of 5/21/2024 | DAL13 | 3 | Data Hall 2 | 2250 | 400/30/3Phase
Power Readings | C:\Users\4G5597897\Box\IBM Cloud Capacity\Capacity Management - Shared Reports\DC Manager Files\Power Readings\Digital Realty\
Rack Power Calculator | C:\Users\4G5597897\Box\IBM Cloud Capacity\DC Files\DC - Rack Power Calculator\